Sec. 1728.202  RUS Bulletin 1728H-702, RUS Specification for Quality 

          Control and Inspection of Timber Products.

    (a) Scope. This specification describes in more detail the 

responsibilities and procedures pertaining to quality control for 

crossarms, as specified in Sec. 1728.201 of this part, and poles, 

covered in RUS Bulletin 1728F-700, incorporated by reference in 

Sec. 1728.97 of this part and in Sec. 1755.97 of 7 CFR part 1755.

    (b) Related specifications and standards incorporated by reference. 

The following specifications and standards referenced throughout this 

section are incorporated by reference. This incorporation by reference 

is approved by the Director of the Federal Register in accordance with 5 

U.S.C. 552(a) and 1 CFR part 51. Copies of each are available for 

inspection during normal business hours at RUS, room 1250-S, U.S. 

Department of Agriculture, Washington, DC 20250 or at the Office of the 

Federal Register, 800 North Capitol Street, NW., suite 700, Washington, 

DC. Copies of these standards and specifications may be purchased from 

the addresses shown below.

    (1) American Wood-Preservers' Association (AWPA), Book of Standards, 

1991 edition, available from AWPA, P.O. Box 286, Woodstock, Maryland 

21163-0286.

    (i) A1-91, Standard for Coal Tar Creosote for Land and Fresh Water 

Use.

    (ii) A2-91, Standard Methods for Analysis of Waterborne 

Preservatives and Fire-Retardant Formulations.

    (iii) A3-91, Standard Methods for Determining Penetration of 

Preservatives and Fire Retardants.

    (iv) A5-91, Standard Methods for Analysis of Oil-Borne 

Preservatives.

    (v) A6-89, Method for the Determination of Water and Oil-Type 

Preservatives in Wood.

    (vi) A7-75, Wet ashing Procedure for Preparing Wood for Chemical 

Analysis.

    (vii) A9-90, Standard Method for Analysis of Treated Wood and 

Treating Solutions by X-Ray Emission Spectroscopy.

    (viii) A11-83, Analysis of Treated Wood and Treating Solutions by 

Atomic Absorption Spectroscopy.

    (ix) C1-91, Standard for Preservative Treatment by Pressure 

Processes All Timber Products.

    (x) C4-91, Standard for the Preservative Treatment of Poles by 

Pressure Processes.

    (xi) C8-91, Standard for the Full-Length Thermal Process Treatment 

of Western Red Cedar Poles.

    (xii) C10-91, Lodgepole Pine Poles--Preservative Treatment by the 

Full-Length Thermal Process.

    (xiii) C12-90, Western Larch Poles--Full-Length preservative 

Treatment by Thermal Process.

    (xiv) M1-90, Standard for the Purchase and Preservation of Forest 

Products.

    (xv) M2-91, Standard Instructions for the Inspection of Preservative 

Treatment of Wood.

    (xvi) M3-81, Standard Quality Control Procedures for Wood Preserving 

Plants.

    (xvii) M4-91, Standard for the Care of Preservative-Treated Wood 

Products.

    (xviii) P1/P13-91, Standard for Coal Tar Creosote for Land and, 

Fresh Water and Marine (Coastal Water Use).

    (xix) P5-91, Standards for Water-Borne Preservatives.

    (xx) P8-91, Standards for Oil-Borne Preservatives.

    (xxi) P9-91, Standards for Solvents for Organic Preservative 

Systems.

    (2) American Institute of Timber Construction (AITC) 200-83, 

Inspection Manual, 1987 edition, available from AITC, 333 West Hampden 

Avenue, Englewood, Colorado 80110.

    (3) American National Standards Institute (ANSI) 05.2-1983, American 

National Standard for Wood Products--Structural Glued Laminated Timber 

for Utility Structures, available from ANSI, 1430 Broadway, New York, 

New York 10018.

    (4) American National Standards Institute/American Institute of 

Timber Construction (ANSI/AITC) A190.1-1983, American National Standard 

for Wood Products--Structural Glued Laminated Timber, available from 

ANSI, 1430 Broadway, New York, New York 10018.

    (5) American Society for Testing and Materials (ASTM) D9-87 (1992), 

Standard Terminology Relating to Wood, available from ASTM, 1916 Race 

Street,

[[Page 298]]

Philadelphia, Pennsylvania 19103-1187, telephone number (215) 299-5585.

    (c) General stipulations. (1) Each RUS electric borrower shall 

submit to the Director, Electric Staff Division, Rural Utilities 

Service, room 1250-S, 14th and Independence Avenue, SW., Washington, DC 

20250-1500, in January of each year a list of plants from which it 

obtained poles or crossarms during the preceding calendar year.

    (2) Ultimate quality control is the responsibility of the producer's 

management; however, a member of the producer's staff shall be 

designated quality control designee and charged with the responsibility 

for the exercise of proper quality control procedures. The requirements 

in American Wood Preservers' Association (AWPA) Standard M3, covering 

records, adequate laboratory, plant gauges, and other plant facilities 

including proper storage, shall be followed.

    (3) The methods of inspection described in this section shall be 

used no matter which plan timber products are purchased under, i.e., 

Insured Warranty Plan, Independent Inspection Plan, or Quality Assurance 

Plans as described in Sec. 1728.201 of this part or RUS Bulletin 1728F-

700. The number of poles and crossarms actually inspected by monitors 

for quality control under a Quality Assurance Plan or the Insured 

Warranty Plan may vary from the number of poles and crossarms inspected 

under the Independent Inspection Plan. Under the Independent Inspection 

Plan, each pole and a sample number of crossarms shall be inspected.

    (4) Under the Independent Inspection Plan, the RUS borrower should 

designate in the purchase order which inspection agency it has selected. 

Unless the RUS borrower contracts for inspection as a separate 

transaction, the treating company shall obtain the services of the RUS 

borrower's designated inspection agency. For reserve treated stock for 

purchase under the Independent Inspection Plan, the treating company 

shall obtain the services of an inspection agency. Selection of and 

changes in inspection agencies for reserve treated stock shall be 

promptly reported to the Director, Electric Staff Division, Rural 

Utilities Service, Washington, DC 20250-1500, in accordance with RUS 

Bulletin 1728F-700, and Sec. 1728.201.

    (5) Individual inspectors in the employ of Independent Inspection 

Agencies shall be experienced and competent. The inspector shall perform 

all phases of the inspection personally and in the proper sequence. The 

primary responsibility of the inspector is to determine, for the 

borrower, by careful inspection and verification, that the timber 

products, preservative, and treatment meet the requirements of RUS 

Bulletin 1728F-700 and Bulletin 1728H-701 and that the methods, storage 

facilities, and production equipment conform to applicable RUS 

specifications. For details of the recommended inspector's 

qualifications see appendix A of this section.

    (6) Laminated materials for use on RUS borrower systems shall follow 

manufacturing and quality control requirements as specified in ANSI 

05.2--1983, American National Standard for Wood Products--Structural 

Glued Laminated Timber for Utility Structures, and ANSI/AITC A190.1-

1983, American National Standard for Wood Products--Structural Glued 

Laminated Timber. The product shall be marked and certified.

    (i) Laminated material shall be inspected by a qualified inspection 

and testing agency.

    (ii) Quality control of material shall be performed to determine 

conformance with Sec. 1728.201 of this part and AITC 200-83, Inspection 

Manual.

    (d) Quality control and inspection procedures for product 

acceptance. It is the responsibility of the plant quality control 

designee to perform the following procedures to insure that a particular 

lot of material conforms to the requirements of the applicable RUS 

specification prior to treatment. After the plant quality control 

designee has performed these procedures, a particular lot of material 

shall be released to the inspector for verification of conformance.

    (1) Poles can be purchased under any of the three purchase plans. 

These plans are Insured Warranty Plan, Independent Inspection Plan, or a 

Quality Assurance Plan. Under the Independent Inspection Plan, all poles 

in a lot shall

[[Page 299]]

be inspected. Under the Insured Warranty Plan and a Quality Assurance 

Plan, the number of poles in a lot actually inspected may be less than 

every pole, depending on the terms of the plans.

    (i) Ample space and assistance shall be provided by the treating 

plant for handling and turning to insure that the surfaces of all items 

can be adequately inspected.

    (ii) Under the Independent Inspection Plan, all poles shall be 

inspected for conformance to the requirements of RUS Bulletin 1728F-700. 

If a pole is rejected and the cause of rejection is corrected, the 

rejected pole may be offered again for inspection as new material.

    (iii) Dimensions, length, and circumference shall be measured by a 

standard steel pole tape to determine that they are in agreement with 

the details for class and length in the brand and butt stamp. If it is 

obvious by visual comparison with a measured pole that the brand 

information is correct, individual poles need not be measured. Pole 

circumference dimensions made prior to treatment shall govern 

acceptance. Reduction in dimension due to treatment and shipping shall 

be not more than 2 percent below the minimum for the pole class.

    (iv) If 15 percent of the poles in a lot offered for inspection are 

defective, the inspector shall terminate the inspection. Re-examination 

of an entire lot by plant quality control shall be required when the 

number of rejected poles equals or exceeds 15 percent of the lot 

inspected. All defective or nonconforming poles either shall be removed 

from the lot or marked out.

    (v) Poles in a lot inspected for decay shall be of the same 

seasoning condition. If the independent inspector suspects that decay 

has occurred, he shall cut a slice from both ends for closer 

examination. If 5 percent of the inspected poles in a lot shows evidence 

of decay, the entire lot shall be unconditionally rejected without 

further sorting.

    (vi) Moisture content, when limited by the purchaser, as stated on 

the borrower's purchase order, shall be measured by calibrated electric 

moisture meter. Calibration of the meter shall include not only the zero 

settings for the X and Y readings, but also two resistance standards for 

12 and 22 percent moisture content.

    (vii) Material failing to conform for moisture content may be 

retested upon request after a recalibration of the instrument. The 

results of the second test shall govern disposition of the lot.

    (viii) Re-examination for any mechanical damage or deterioration and 

for original acceptance shall be conducted on timber products not 

treated within 10 days after original inspection.

    (2) Crossarms can be purchased only under either of two purchase 

plans. These plans are the Independent Inspection Plan or Quality 

Assurance Plans. Under the Independent Inspection Plan, crossarms are to 

be inspected prior to manufacture, during manufacture, and after 

treatment. Under a Quality Assurance Plan, crossarms are monitored 

according to the terms of the quality assurance program acceptable to 

RUS.

    (i) Inspection prior to treatment shall include:

    (A) Surface inspection of all ends of all arms. This is usually done 

on the stacks of arms prior to manufacture. Particular attention shall 

be paid to defects commonly found in the ends, such as compression wood, 

red heart and other forms of decay, shakes, splits, through checks, 

scantiness, honeycomb, and low density, determined by rings per inch 

(centimeter) and percent of summerwood. Whenever the number of 

nonconforming arms is found to exceed 0.5 percent of the lot or one arm, 

whichever is greater, the entire lot shall be rejected for excess number 

of defective ends. After the producer has removed or marked out the 

defective material, the arms may be resubmitted for inspection.

    (B) Surface inspection of the lengthwise sides performed on a random 

representative sample. The sample size shall equal 20 percent of a lot 

size or 200 arms, whichever is smaller. The inspector shall examine side 

surfaces as they are slowly rotated. When necessary, the rotation may be 

stopped for closer inspection. Whenever the number of nonconforming arms 

is found to exceed 2 percent of the sample size, the entire lot shall be 

rejected. After the producer has removed or marked out

[[Page 300]]

the defective material, the arms may be resubmitted for inspection.

    (C) Check of moisture content of the random sample by a calibrated 

moisture meter.

    (D) Check of crossarm dimensions of the random sample measured after 

surfacing.

    (ii) Inspection during manufacture shall consist of:

    (A) Checking bolt and insulator pin holes for squareness and 

excessive splintering;

    (B) Checking brands for completeness, location, and legibility; and

    (C) Checking arms for conformance.

    (iii) Under the Independent Inspection Plan, there shall be a final 

inspection during and after treatment for preservative retention and 

penetration and for damage.

    (3) Structural glued laminated timber shall be tested and inspected 

in accordance with AITC 200-83, Inspection Manual. Grade of lumber shall 

be inspected by a qualified grader for specified quality, and so marked, 

in accordance with grading rules of the American Lumber Standards. 

Adhesives used for all structural arms shall meet requirements of ANSI 

05.2-83, paragraph 5.2. Melamine urea adhesives shall not be used. End 

joint spacings and limitations shall be in accordance with ANSI 05.2-83.

    (e) Preservatives. (1) Creosote shall conform to the requirements of 

AWPA Standard P1 when analyzed by AWPA Standard Al, sections 2, 3, 4, 

either 5 or 9, and 6.

    (i) Each occasional charge, all material treated in a cylinder at 

one time, shall be analyzed.

    (ii) The first charge and one of every five charges randomly 

selected in consecutive charges shall be analyzed.

    (2) Solutions of waterborne preservatives shall be analyzed for 

components in accordance with AWPA Standards A2, A9, or A11, and shall 

meet the requirements of P5 for composition. AWPA A2 shall be used as a 

referee method.

    (3) Pentachlorophenol shall contain not less than 95 percent 

chlorinated phenols and conform to AWPA Standard P8 in hydrocarbon 

solvent AWPA P9 Type A.

    (4) Copper Naphthenate in hydrocarbon solvent (AWPA P9 Type A) shall 

contain not less than 6 percent nor more than 8 percent copper in the 

form of Copper Naphthenate and conform to AWPA Standard P8 when analyzed 

in accordance with AWPA Standard A5.

    (f) Plant facilities and inspection during treatment. (1) 

Manufacturing and treating plant facilities shall conform to AWPA 

Standard M3, paragraph 3. Pressure plants shall be equipped with 

recording instruments to register time, pressure, temperature and vacuum 

during each cycle of treatment. They shall also be equipped with 

indicating thermometers and pressure and vacuum gauges to check the 

accuracy of the recorders. Work tanks shall be equipped with a 

thermometer. Thermal treating vats shall be equipped with a time and 

temperature recorder and with an indicating thermometer. Temperature 

recording devices are not mandatory for plants treating exclusively with 

waterborne preservatives.

    (2) Under the Independent Inspection Plan, the inspector shall be 

present during the treatment procedure, except at times when it may be 

impractical, such as during late night or early morning treatments. At 

such times, temperature, pressure, and vacuum data shall be taken from 

the recording charts.

    (3) Recording instruments shall be checked with indicating gauges 

and thermometers. Inaccuracies shall be referred to the treating company 

for prompt correction. In the event of an inaccuracy, indicating 

possible damage to the material, the inspector shall reject the charge.

    (g) Results of treatment. (1) Poles shall be tested for retention 

and penetration by means of a calibrated increment borer 0.2 inches 

(0.51 cm) [plusmn]0.02 inches (0.05 cm) in diameter in accordance with 

procedures in AWPA Standard M2, paragraph 5.22. Under the Independent 

Inspection Plan, all treating charges shall be tested for retention and 

penetration. Plant quality control and independent inspection shall do 

their analyses separately. Under the Insured Warranty Plan and Quality 

Assurance Plans, the frequency of testing retention and penetration may 

vary according to the plan.

[[Page 301]]

    (i) Western red and northern white cedars and western larch poles 

shall be bored at any point of the periphery approximately 6-12 inches 

(15.24-30.48 cm) above ground line and all other species approximately 1 

foot (30.48 cm) above or below the brand.

    (ii) Penetration shall be determined in accordance with AWPA 

Standard A3. Chrome Azurol S and Penta-Check shall be used to determine 

penetration of copper containing preservatives and penta, respectively.

    (iii) Retention sampling. (A) When there are 20 or more poles in the 

treating charge, the retention sample for creosote shall consist of 20 

assay zones from southern pine and Douglas-fir poles. All poles in 

charges with fewer than 20 poles shall be bored once. Charges with less 

than 15 poles shall be bored once and bored again on a random basis to 

obtain a minimum of 15 assay zones.

    (B) Retention samples shall be taken from 20 poles in charges of 20 

or more poles.

    (C) Retention samples for Alaska yellow, western red, and northern 

white cedars shall be comprised of a minimum of 30 assay zones for 

creosote and waterborne preservatives. For penta charges of fewer than 

30 poles, the sample shall contain the assay zone from each pole in the 

lot.

    (D) Retention samples shall be comprised of borings, representative 

of pole volumes for each class and length in the charge. Further 

selection and marking of poles of mixed seasoning, volume, and location 

on the tram shall be made as illustrated in the following table:

------------------------------------------------------------------------

                                                  Vol.            Number

       Number of Poles           Class/Length    in cu.   Total     of

                                                   ft.   Volume  Borings

------------------------------------------------------------------------

27                             7/30(09.1 m)      232     15      3

26                             4/35(10.7 m)      447     29      6

11                             5/35(10.7 m)      163     10      2

55<SUP>[ast]</SUP>                        6/35(10.7 m)      704     46      9

                                                --------

          Total..............  ................  1,546   ......  .......

------------------------------------------------------------------------

*If a portion of these poles were green and some partially seasoned,

  then the number of borings should reflect the approximate percentage

  of each.

    (iv) When material in a lot consists of fewer pieces than the 

designated minimum number of samples for assay, additional borings shall 

be taken so as to make up at least the minimum sample, and in such 

manner that the sample is representative of the lot of material with 

respect to any variations in size, seasoning condition, or other 

features that might affect the results of treatment.

    (v) Analyses for preservative retention shall be performed.

    (A) Creosote shall be analyzed by AWPA Standard A6.

    (B) Penta shall be analyzed by AWPA Standard A5 or A9. Copper 

pyridine method is required when timber may have been in contact with 

salt water and for all species native to the Pacific coast region, 

unless the raw material invoice specifically states that the material 

either has not been in contact with salt water or has been shown by 

analysis to have contained no additional chlorides before treating.

    (C) Copper Naphthenate shall be analyzed by tests in accordance with 

AWPA Standards A5 or A9.

    (D) Waterborne preservatives shall be analyzed by tests in 

accordance with AWPA Standards A2, A7, A9, or A11.

    (E) Prior to unloading a tram, the inspectors may take their own 

samples and analyze them concurrently with the quality control designee, 

but each shall work independently, and quality control data shall be 

presented before acceptance of the charge.

    (vi) Penetration sampling of poles. (A) Group A poles consist of 

poles with a circumference of 37.5 inches (95.25 cm) or less at 6 feet 

(1.8 m) from butt.

    (1) Bore 20 Group A poles or 20 percent of the poles, whichever is 

greater. Accept if 100 percent of the sample conform; otherwise, bore 

all poles.

    (2) Re-treat the charge if more than 15 percent of the borings are 

found to be nonconforming.

    (3) Re-treat all nonconforming poles if 15 percent or fewer fail the 

requirement.

    (B) Group B poles consist of poles with circumference greater than 

37.5 inches (95.25 cm) at 6 feet (1.8 m) from the butt.

    (1) For Group B poles 50 feet (15.2 m) and shorter, bore each pole 

and re-treat only those found to be nonconforming, unless more than l5 

percent fail; in that case, re-treat the entire lot.

[[Page 302]]

    (2) For Group B poles longer than 50 feet (15.2 m), bore each pole 

twice at 90 degrees apart around the pole and accept only those poles 

conforming to the penetration requirement in both borings. All 

nonconforming poles may be re-treated only twice.

    (vii) All holes (nominal 0.2 of an inch (0.05 cm) diam. bit) shall 

be promptly filled with treated, tight-fitting wood plugs.

    (2) Under the Independent Inspection Plan, all treating charges of 

crossarms shall be tested for retention and penetration. Plant quality 

control inspectors and independent inspectors shall do their analyses 

independently. Under the Quality Assurance Plans, the frequency of 

testing retention and penetration may vary according to the plan.

    (i) The penetration and retention sample shall consist of 20 (48 for 

creosote) outer 6/10 of an inch (1.52 cm) for Douglas-fir and 1 inch 

(2.54 cm) for Southern Yellow Pine zones from borings taken from any 

face except the top face at a location as close to the end as possible 

being at least 3 inches (7.62 cm) from the end of the arm and no closer 

than 3 inches from the edge of any holes. For laminated material, 

borings shall be taken from laminates on a random basis.

    (ii) Penetration shall be tested by taking not less than 20 borings 

from 20 crossarms in each charge, determined in accordance with AWPA 

Standard A3. Chrome Azurol S and Penta-Check shall be used to determine 

penetration of copper containing preservatives and penta, respectively.

    (3) Laminated material shall be checked for any evidence of 

delamination due to treatment and for the identifying quality stamp of 

AITC or American Plywood Association (APA).

    (4) When x-ray fluorescence (XRF) instruments are used to analyze 

preservative or retention, Periodic Instrument Checks (PIC) shall be 

made by the treating plant and any outside inspection agency using the 

treating plant's instrument or its own. Appendix B of this section 

outlines a recommended procedure.

    (5) At a minimum, treating plants shall perform the PIC weekly and 

record the results in the instrument's log, which shall be stored with 

the instrument. Independent inspection agencies shall use their own 

samples to perform the PIC on treater's instrument once per visit, not 

to exceed one PIC per week. Inspection agencies shall record their 

results in the instrument's log and state the date of its latest PIC on 

all treating reports.

    (6) XRF instruments shall be accurate and reliable, and they shall 

generate reproducible results. Instruments shall have thorough 

instructions which should include recommendations on drying techniques, 

equipment, and density calculations. These drying recommendations shall 

be followed when using these instruments.

    (h) Product acceptance. Under the Independent Inspection Plan, the 

inspector shall signify acceptance by marking each piece of accepted 

material with a clear, legible hammer stamp in one end prior to 

treatment and in the other end after treatment. The inspector shall 

personally mark each piece, and shall not delegate this responsibility 

to another person.

    (i) Charge inspection reports. (1) Inspection Reports shall cover 

the following:

    (i) The total pieces in the lot, number of and causes for rejection;

    (ii) The conditioning of the material prior to treatment;

    (iii) The analyses of preservative identified by the analyst's 

signature or certification;

    (iv) The details of treatment; and

    (v) The results of treatment. These results shall include the 

following:

    (A) The depth of penetration for retention sample and a summary of 

all poles rejected for insufficient penetration;

    (B) Worksheets for retention analyses, each identified by quality 

control designee and independent inspector;

    (C) The number of pieces offered and rejected, together with the 

cause(s) for rejection;

    (D) The date of latest Periodic Instrument Check.

    (2) On each inspection report the independent inspector and the 

plant quality control designee shall certify, in writing, that the 

material listed on the report has been inspected before,

[[Page 303]]

during, and after treatment, and that the preservative used was analyzed 

in accordance with the requirements of this section.

    (3) Each inspector or inspection agency shall retain for a period of 

1 year a copy or transcript of each report of inspection, together with 

laboratory worksheets covering retention by assay and preservative 

analyses for the purchaser, and on request shall furnish a copy or 

transcript of any of these reports to the Director, Electric Staff 

Division, Rural Utilities Service, Washington, DC 20250-1500.

    (j) Charge numbers on re-treat poles. The letter ``R'' shall be 

added to the original charge number in the butts of all poles that are 

re-treated for insufficient penetration or retention of preservative. 

All poles that fail to meet treatment requirements after two re-

treatments shall be permanently rejected.

    (k) Safety provisions. Poles intended for RUS borrowers shall not be 

inspected when, in the opinion of the inspector, unsafe conditions are 

present.

   Appendix A to Sec. 1728.202--Recommended Inspectors' Qualifications

    (a) Inspection agencies should see that inspectors assigned to the 

inspection of timber products and treatment for RUS borrowers are 

competent and experienced.

    (b) Recommended experience. In general, any of the following 

examples are recommended as minimum qualifying experience before a new 

inspector may be permitted to inspect timber products for RUS borrowers:

    (1) Three years' experience as an inspector of timber and the 

preservative treatment of timber.

    (2) Three years' experience in timber treating plant quality control 

work.

    (3) Under the direct supervision of an experienced, well-qualified 

inspector, who has performed the following:

    (i) Inspected at least 2,500 poles and/or crossarms ``in the 

white.''

    (ii) Checked preservative penetration results on at least 500 poles 

and crossarms.

    (iii) Made at least 35 wood assays for preservative retention.

    (iv) Made at least 25 analyses of each type preservative used on 

material the person is assigned to inspect.

    (v) In both (b)(1) and (b)(2) of this appendix A, the experience 

should be not less than that required in (b)(3)(i), (b)(3)(ii), 

(b)(3)(iii), and (b)(3)(iv).

    (4) Inspectors experienced in the inspections of one product, such 

as poles, should not be qualified to inspect another product, such as 

crossarms, until the above experience is gained.

    (5) The inspector should be especially well informed in wood 

preservation and the operation of a timber treating plant, and be 

competent in preservative analysis and other laboratory work.

    (6) In all cases, an inspector should be thoroughly instructed in 

the application of RUS specifications and the standards pertaining 

thereto before being permitted to independently inspect timber products 

and the treatments applied to them. Knowledge of these specifications 

and standards, as well as the inspector's proficiency, may be checked 

routinely by members of the RUS staff.

      Appendix B to Sec. 1728.202--Periodic Instrument Check X-ray 

                              Fluorescence

    (a) General. The following sample calibration standards and 

procedures may be used in lieu of comparison with analysis by wet ash or 

lime ignition methods.

    (b) Penta. Until such time as AWPA approves calibration standards 

for penta, the following method should be used to run a salt water 

solution to measure Cl (chloride).

    (1) Standard Solution. Dry approximately 15 grams of reagent grade 

NaCl at 105[deg]C for 1 hour. Weigh 10.00 grams into a tared beaker. Add 

distilled water until the total weight is 100.00 grams. Stir until 

completely dissolved. This will give a 10 percent weight to weight 

solution of NaCl.

    (2) Baseline Check. (i) Insure that the instrument is in good 

agreement with lime ignition.

    (ii) Record any user correction factors.

    (iii) Stabilize and standardize the instrument.

    (iv) Run the salt solution five times using the PENTA-OIL 

calibration mode.

    (v) Record the average and standard deviation of the values for 

percent penta. The average value will now be considered the nominal 

value.

    (3) Periodic Instrument Check. Run the salt solution two times and 

average the results. If the value is more than [plusmn]5 percent of the 

nominal value, the instrument needs further calibration, following 

manufacturer's recommendation.

    (c) Waterborne preservatives. Treaters and inspection agencies 

should purchase AWPA Committee P-5 Standard Reference Materials to 

analyze on their instruments. Reference materials should be in the 

retention range of the material being produced at the plants. If the 

value is more than [plusmn]5 percent of the nominal value, the 

instrument needs further calibration. AWPA Committee P-5 Standard 

Reference Materials may be purchased from:

[[Page 304]]

American Wood Preservers' Association, P.O. Box 286, Woodstock, Maryland 

21163, Phone: (410) 456-3169.

[58 FR 41406, Aug. 3, 1993]

