## AC-Heat Pump
ENERGY STAR in Cooperation with ABC Electric Company Installation Commissioning Report for Central AC and Heat Pump | [29 empty] | OMB Control No. xxxx-xxxx
Site Information
Customer name (name on electric bill):
Customer electric utility account number:
Address:
| City: | [14 empty] | State: | [6 empty] | Zip:
Design
| Type of installation: |  |  |  |  | q | Replacement |  |  |  |  | q | New system - existing home | [8 empty] | q | New system - new home
[6 empty] | q | AC only |  |  |  |  | q | Heat only | [8 empty] | q | AC & heat
| Area of zone served by unit: | [13 empty] | sq ft |  |  |  | # of units in home:
Is the unit self-contained, or is fan/airflow provided by external device (furnace)?
| Heat gain method: |  |  |  |  | q | Manual J v7 |  |  |  | q | Manual J v8 |  |  |  | q | None |  |  | q | Other:
| Duct design method: |  |  |  |  | q | Manual D |  |  |  | q | None |  |  |  | q | Other:
| Equipment specification method: | [8 empty] | q | Manual S |  |  |  | q | OEM recommendation | [6 empty] | q | Other:
| Latent heat gain: | [11 empty] | BTUh |  |  |  | Sensible heat gain: | [10 empty] | BTUh
| Total heat gain: | [11 empty] | BTUh |  |  |  | Design airflow: | [10 empty] | CFM
| Duct design static pressure: | [11 empty] | IWC |  |  |  | Design heat loss: | [10 empty] | BTUh
Equipment
| Condenser |  |  | Manufacturer: | [15 empty] | Model:
Serial number:
| Evaporator |  |  | Manufacturer: | [15 empty] | Model:
Serial number:
| System |  |  | Metering device: |  |  |  |  | q | TXV |  |  | q | Fixed orifice |  |  |  | q | Other:
|  |  |  | Refrigerant: |  |  |  |  | q | R-22 |  |  | q | R-410a |  |  |  | q | Other:
| Fan Motor Type: |  |  |  | q | Fixed speed (e.g. PSC) | [6 empty] | q | Variable (e.g. ECM/ICM) | [6 empty] | q | Other:
| Cooling |  |  | Latent Capacity: | [9 empty] | BTUh |  |  |  | ARI EER/SEER:
|  |  |  | Sensible Capacity: | [9 empty] | BTUh |  |  |  | ARI Ref #:
|  |  |  | Total Capacity: | [9 empty] | BTUh
| Heating |  |  | HSPF:
|  |  |  | At 17oF |  |  |  | Capacity: | [8 empty] | BTUh |  |  |  | COP:
|  |  |  | At 47oF |  |  |  | Capacity: | [8 empty] | BTUh |  |  |  | COP:
Previous equipment - for replacements only
|  | Cooling |  |  |  | Total capacity: | [7 empty] | Btuh |  |  |  | ARI EER/SEER:
|  | Heating |  |  |  | HSPF:
[6 empty] | At 17oF |  |  |  | Capacity: | [8 empty] | BTUh |  |  |  | COP:
[6 empty] | At 47oF |  |  |  | Capacity: | [8 empty] | BTUh |  |  |  | COP:
AC & Heat Pump Installation Commissioning Report (Page 2 of 3)
Equipment - continued
Does capacity meet requirement of 95-115% (or up to 125% for heat pumps with heat dominated requirements)
| of calculated load or the next nominal size? | [11 empty] | q | Yes |  | q | No
Refrigerant Tests - run system for 15 minutes before testing
| Date: | [11 empty] | Outdoor ambient temp. (at condenser): | [14 empty] | oF DB
| Time of test: | [11 empty] | Outdoor relative humidity - optional:
Barometric pressure - optional:
Air temperatures measured in duct near evaporator (not in conditioned building space):
|  |  | Cooling Mode |  |  |  |  | Return | [7 empty] | oF DB | [7 empty] | oF WB
[8 empty] | Supply | [7 empty] | oF DB | [7 empty] | oF WB
|  |  | Heating Mode |  |  |  |  | Return | [7 empty] | oF DB
[8 empty] | Supply | [7 empty] | oF DB
| Liquid line pressure: | [9 empty] | psi |  |  |  |  | Liquid line temp.: | [10 empty] | oF DB
| Suction line pressure: | [9 empty] | psi |  |  |  |  | Suction line temp.: | [10 empty] | oF DB
| Refrigerant Calculations | [6 empty] | Condenser sat. temp. (from liquid pressure): | [15 empty] | oF DB
[8 empty] | Evaporator sat. temp. (from suction pressure): | [15 empty] | oF DB
| Subcooling (condensing temp. - liquid line temp.): | [15 empty] | oF DB
| Superheat (suction line temp. - evaporating temp.): | [15 empty] | oF DB
For TXV
|  | OEM subcooling goal: | [8 empty] | oF DB
|  | Subcooling deviation (subcooling - subcooling goal): | [15 empty] | oF DB
For Fixed Orifice
|  | Superheat goal (from superheat lookup tables, based on outdoor ambient and return air wet bulb temps.): | [25 empty] | oF DB
|  | Superheat deviation (superheat goal - superheat): | [15 empty] | oF DB
| Does system meet requirement of subcooling within ±3oF or superheat within ±5oF of goal? | [23 empty] | q | Yes |  | q | No
Electrical Measurements - taken at time of refrigerant tests
| Evaporator/air handler fan: | [10 empty] | amps | [6 empty] | volts | [6 empty] | watts
| Condenser fan: | [10 empty] | amps | [6 empty] | volts | [6 empty] | watts
| Compressor: | [10 empty] | amps | [6 empty] | volts | [6 empty] | watts
Electrical Requirements
| Does system meets requirements of ACCA QI 4.3? | [13 empty] | q | Yes |  | q | No
Air Flow Tests
| Date: | [11 empty] | Outdoor ambient temp. (at condenser): | [14 empty] | oF DB
| Time of test: | [11 empty] | Outdoor relative humidity - optional:
Barometric pressure - optional:
| Measured air volume at evaporator: | [12 empty] | CFM
AC & Heat Pump Installation Commissioning Report (Page 3 of 3)
Air Flow Tests - continued
| Test peformed in heating or cooling mode? | [11 empty] | q | Heating |  |  | q | Cooling
| Static pressure |  |  |  | Return |  |  | Static: | [5 empty] | IWC |  | Measurement location:
[5 empty] | Supply |  |  | Static: | [5 empty] | IWC |  | Measurement location:
| Measurement method used: | [6 empty] | q | TrueFlow |  |  | q | Pressure matching (with Duct Blaster) | [9 empty] | q | Anemometer
[8 empty] | q | Fan Curve |  |  | q | Temperature split (heating only) | [9 empty] | q | Other:
| Speed Setting |  |  |  | If fixed |  | qLow qMed-Low qMed qMed-High qHigh | [15 empty] | CFM (at 0.5 IWC):
[5 empty] | If variable |  |  |  | Fan set for | [6 empty] | CFM/ton
| Does air flow meet requirement of 350-450 cfm or within range recommended by OEM? | [23 empty] | q | Yes |  | q | No
Duct Leakage
| Initial Test |  |  |  | Date: | [10 empty] | Time:
| Final Test |  |  |  | Date: | [10 empty] | Time:
| Test method used: |  |  |  |  | q | Duct Blaster |  |  |  | q | Blower Door Subtraction | [7 empty] | q | Other:
| Existing system duct leakage: | [10 empty] | CFM
| Post Installation duct leakage: | [10 empty] | CFM |  |  |  | Leakage % reduction ([existing-post]/existing):
| Total % leakage (post leakage/design flow): | [12 empty] | OR (post leakage/measured flow):
Does duct leakage meet one of the following requirements:
| existing homes: |  |  |  | q | No more than 20% of total air flow
[5 empty] | q | A reduction of 50% or more from the initial measurement
| new construction: |  |  |  | q | Leakage from ducts inside the thermal envelope is no more than 10% of total air flow
[5 empty] | q | No more than 6% of total air flow from ducts outside the thermal envelope
[5 empty] | q | Less than 4 CFM leakage to outdoors per 100 square feet of conditioned floor area
System Controls
| Does system meets requirements of ACCA QI 4.6? | [13 empty] | q | Yes |  | q | No
System Documentation & Owner Education
| Copies of this report and OEM manuals left with owner? | [14 empty] | q | Yes |  | q | No
| Demonstrated system for owner? | [8 empty] | q | Yes |  | q | No
Contractor/Technician Information
Technician name:
Company:
Address 1:
Address 2:
| City: | [15 empty] | State: | [6 empty] | Zip:
Phone/Email:
Technician signature:
Please send completed forms to: System Implementer, 123 Main St, Town, ST, 01234, FAX 555-123-4567
EPA Form 5900-180
The government estimates the average time needed to fill out this form is 1.00 hour and welcomes suggestions for reducing this effort.
Send comments (referencing OMB Control Number) to the Director, Collection Strategies Division, U.S. EPA (2822T), 1200 Pennsylvania Ave., NW, Washington, D.C. 20460.

## AC-Furnace
ENERGY STAR in Cooperation with ABC Electric Company Installation Commissioning Report for Central AC and Furnace
Site Information
Customer name (name on electric bill):
Customer electric utility account number:
Address:
| City: | [14 empty] | State: | [6 empty] | Zip:
Design
| Type of installation: |  |  |  |  | q | Replacement |  |  |  |  | q | New system - existing home | [8 empty] | q | New system - new home
[6 empty] | q | AC only |  |  |  |  | q | Heat only | [8 empty] | q | AC & heat
| Area of zone served by unit: | [13 empty] | sq ft |  |  |  | # of units in home:
| Heat gain method: |  |  |  |  | q | Manual J v7 |  |  |  | q | Manual J v8 |  |  |  | q | None |  |  | q | Other:
| Duct design method: |  |  |  |  | q | Manual D |  |  |  | q | None |  |  |  | q | Other:
| Equipment specification method: | [8 empty] | q | Manual S |  |  |  | q | OEM recommendation | [6 empty] | q | Other:
| Latent Heat Gain: | [11 empty] | BTUh |  |  |  | Sensible Heat Gain: | [10 empty] | BTUh
| Total Heat Gain: | [11 empty] | BTUh |  |  |  | Design Airflow: | [10 empty] | CFM
| Duct Design Static Pressure: | [11 empty] | IWC |  |  |  | Design heat loss: | [10 empty] | BTUh
Equipment - AC
| Condenser |  |  | Manufacturer: | [15 empty] | Model:
Serial number:
| Evaporator |  |  | Manufacturer: | [15 empty] | Model:
Serial number:
| System |  |  | Metering device: |  |  |  |  | q | TXV |  |  | q | Fixed orifice |  |  |  | q | Other:
|  |  |  | Refrigerant: |  |  |  |  | q | R-22 |  |  | q | R-410a |  |  |  | q | Other:
| Fan Motor Type: |  |  |  | q | Fixed speed (e.g. PSC) | [6 empty] | q | Variable (e.g. ECM/ICM) | [6 empty] | q | Other:
| Speed setting |  |  |  | If fixed |  | qLow qMed-Low qMed qMed-High qHigh | [15 empty] | CFM (at 0.5 IWC):
[5 empty] | If variable |  |  |  | Fan set for | [6 empty] | CFM
| Latent Capacity: | [8 empty] | BTUh | [6 empty] | ARI EER/SEER:
| Sensible Capacity: | [8 empty] | BTUh | [6 empty] | ARI Ref #:
| Total Capacity: | [8 empty] | BTUh
Previous equipment - for replacements only
|  | Total capacity: | [7 empty] | Btuh | [6 empty] | ARI EER/SEER:
| Does capacity meet requirement of 95-115% of calculated load or the next nominal size? | [23 empty] | q | Yes |  | q | No
AC & Furnace Installation Commissioning Report (Page 2 of 4)
Equipment - Furnace
| Manufacturer: | [18 empty] | Model:
| Serial number: | [18 empty] | AFUE:
| Gross capacity: | [8 empty] | Btuh |  |  | Net capacity: | [8 empty] | Btuh
Previous equipment - for replacements only
|  | Gross capacity: | [7 empty] | Btuh |  |  | Net capacity: | [8 empty] | Btuh
| Fuel type: |  |  | q | Gas |  | q | Oil |  | q | Propane |  |  |  | q | Other:
| Sealed combustion? |  |  |  |  | q | Yes |  | q | No
| Fan Motor Type: |  |  |  | q | Fixed speed (e.g. PSC) | [6 empty] | q | Variable (e.g. ECM/ICM) | [6 empty] | q | Other:
| Speed Setting |  |  |  | If fixed |  | qLow qMed-Low qMed qMed-High qHigh | [15 empty] | CFM (at 0.5 IWC):
[5 empty] | If variable |  |  |  | Fan set for | [6 empty] | CFM
| Does capacity meet requirement of 100-140% of calculated load or the next nominal size? | [23 empty] | q | Yes |  | q | No
Refrigerant Tests - run system for 15 minutes before testing
| Date: | [11 empty] | Outdoor ambient temp. (at condenser): | [14 empty] | oF DB
| Time of test: | [11 empty] | Outdoor relative humidity - optional:
Barometric pressure - optional:
Air temperatures measured in duct near evaporator (not in conditioned building space):
|  |  | Cooling Mode |  |  |  |  | Return | [7 empty] | oF DB | [7 empty] | oF WB
[8 empty] | Supply | [7 empty] | oF DB | [7 empty] | oF WB
| Liquid line pressure: | [9 empty] | psi |  |  |  |  | Liquid line temp.: | [10 empty] | oF DB
| Suction line pressure: | [9 empty] | psi |  |  |  |  | Suction line temp.: | [10 empty] | oF DB
| Refrigerant Calculations | [6 empty] | Condenser sat. temp. (from liquid pressure): | [15 empty] | oF DB
[8 empty] | Evaporator sat. temp. (from suction pressure): | [15 empty] | oF DB
| Subcooling (condensing temp. - liquid line temp.): | [15 empty] | oF DB
| Superheat (suction line temp. - evaporating temp.): | [15 empty] | oF DB
For TXV
|  | OEM subcooling goal: | [8 empty] | oF DB
|  | Subcooling deviation (subcooling - subcooling goal): | [15 empty] | oF DB
For Fixed Orifice
|  | Superheat goal (from superheat lookup tables, based on outdoor ambient and return air wet bulb temps.): | [25 empty] | oF DB
|  | Superheat deviation (superheat goal - superheat): | [15 empty] | oF DB
| Does system meet requirement of subcooling within ±3oF or superheat within ±5oF of goal? | [23 empty] | q | Yes |  | q | No
AC & Furnace Installation Commissioning Report (Page 3 of 4)
Electrical Measurements - taken at time of refrigerant tests
| Evaporator/air handler fan: | [10 empty] | amps | [6 empty] | volts | [6 empty] | watts
| Condenser fan: | [10 empty] | amps | [6 empty] | volts | [6 empty] | watts
| Compressor: | [10 empty] | amps | [6 empty] | volts | [6 empty] | watts
Electrical Requirements
| Does system meets requirements of ACCA QI 4.3? | [13 empty] | q | Yes |  | q | No
Air Flow Tests
| Date: | [11 empty] | Outdoor ambient temp. (at condenser): | [14 empty] | oF DB
| Time of test: | [11 empty] | Outdoor relative humidity - optional:
Barometric pressure - optional:
| Measured air volume at evaporator: | [11 empty] | CFM
| Test peformed in heating or cooling mode? | [11 empty] | q | Heating |  |  | q | Cooling
| Static pressure |  |  |  | Return |  |  | Static: | [5 empty] | IWC |  | Measurement location:
[5 empty] | Supply |  |  | Static: | [5 empty] | IWC |  | Measurement location:
| Measurement method used: | [6 empty] | q | TrueFlow |  |  | q | Pressure matching (with Duct Blaster) | [9 empty] | q | Anemometer
[8 empty] | q | Fan Curve |  |  | q | Temperature split (heating only) | [9 empty] | q | Other:
| Does air flow meet requirement of 350-450 cfm or within range recommended by OEM? | [23 empty] | q | Yes |  | q | No
Duct Leakage
| Initial Test |  |  |  | Date: | [10 empty] | Time:
| Final Test |  |  |  | Date: | [10 empty] | Time:
| Test method used: |  |  |  |  | q | Duct Blaster |  |  |  | q | Blower Door Subtraction | [7 empty] | q | Other:
| Existing system duct leakage: | [10 empty] | CFM
| Post Installation duct leakage: | [10 empty] | CFM |  |  |  | Leakage % reduction ([existing-post]/existing):
| Total % leakage (post leakage/design flow): | [12 empty] | OR (post leakage/measured flow):
Does duct leakage meet one of the following requirements:
| existing homes: |  |  |  | q | No more than 20% of total air flow
[5 empty] | q | A reduction of 50% or more from the initial measurement
| new construction: |  |  |  | q | Leakage from ducts inside the thermal envelope is no more than 10% of total air flow
[5 empty] | q | No more than 6% of total air flow from ducts outside the thermal envelope
[5 empty] | q | Less than 4 CFM leakage to outdoors per 100 square feet of conditioned floor area
AC & Furnace Installation Commissioning Report (Page 4 of 4)
Gas Combustion Test
Altitude derating factor (from site elevation):
| Return air: | [7 empty] | oF DB |  |  |  |  | Supply air: | [8 empty] | oF DB
| Orifice size: | [12 empty] | Manifold pressure: | [10 empty] | psi
Gas meter test dial size:
| Gas meter seconds for one revolution of meter: | [12 empty] | Low: | [8 empty] | High:
Gas combustion test calculations
|  | Gas rate (from meter lookup tables): | [8 empty] | Low speed: | [9 empty] | High speed:
|  | Actual firing rate: | [8 empty] | Low speed: | [9 empty] | High speed:
[11 empty] | Percent: | [9 empty] | Percent:
|  | Temperature rise: | [8 empty] | Low speed: | [7 empty] | oF |  | High speed: | [7 empty] | oF
Combustion Analyzer - required for oil systems, optional for other fuels
| O2: | [7 empty] | Stack temperature: | [10 empty] | oF |  | Efficiency:
| CO: | [7 empty] | Draft pressure: | [9 empty] | psi
System Controls
| Does system meets requirements of ACCA QI 4.6? | [13 empty] | q | Yes |  | q | No
System Documentation & Owner Education
| Copies of this report and OEM manuals left with owner? | [14 empty] | q | Yes |  | q | No
| Demonstrated system for owner? | [8 empty] | q | Yes |  | q | No
Contractor/Technician Information
Technician name:
Company:
Address 1:
Address 2:
| City: | [15 empty] | State: | [6 empty] | Zip:
Phone/Email:
Technician signature:
Please send completed forms to: System Implementer, 123 Main St, Town, ST, 01234, FAX 555-123-4567