## Data
Data Start Time. (See Special Instructions on "Copy Data" worksheet). | AGC Scan Rate (seconds) |  | JOU | Non- |  |  | Transferred | Contingent |  |  | Event Detection | Recovery Target Freq: | Max Absolute Delta Hz | Lowest Delta Hz | Highest Delta Hz | Rows of data to shift to align T(0) | [6 empty] | 2.3148e-05 | 3.4722e-05 | 4.6296e-05 | 5.787e-05 | 6.9444e-05
2009-10-12 02:17 | 2 | Net | Dynamic | Conforming | Pumped | Not | Frequency | BA | BA | BA | Row | 60 | 0.126 | -0.126 | 0.033001 | 2 | [6 empty] | 2 Second | 3 Second | 4 Second | 5 Second | 6 Second
|  | Actual | Schedules | Load | Hydro | Used | Response | Lost Generation | Bias | Load | 305 | 40098.1024 | t(0) | [9 empty] | AGC | AGC | AGC | AGC | AGC
|  | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) |  | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | 473 | 40098.1062 | t(Recovery) | Delta | Absolute | [7 empty] | Scan | Scan | Scan | Scan | Scan
Time (T) | Hz | MW | MW | MW | MW |  | MW/0.1 Hz | MW | MW/0.1 Hz | MW | 307 | 0:06 | Event Length mm:ss | Hz | Delta Hz | [7 empty] | Rate | Rate | Rate | Rate | Rate
2009-10-12 02:17 | 60.007 | 3679.946 | 350 | -329.9882 | 0 |  | 10 | 15 | -103 | 7553.79 |  | 0 |  |  |  |  | 350 | -331.853 | 0 | 81.5 | 10 | 15 | 2009-10-12 02:17 | 2009-10-12 02:17 | 2009-10-12 02:17 | 2009-10-12 02:17 | 2009-10-12 02:17
2009-10-12 02:17 | 60.009 | 3679.4399 | 350 | -329.9882 | 0 |  | 10 | 15 | -103 | 7554.12 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -331.853 | 0 | 82 | 10 | 15 | 2009-10-12 02:17 | 2009-10-12 02:17 | 2009-10-12 02:17 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2
2009-10-12 02:17 | 60.009 | 3679.9119 | 350 | -255.4442 | 0 |  | 10 | 15 | -103 | 7554.45 | 0 | 0 | 0 | 0 | 0 |  | 350 | -331.853 | 0 | 82.5 | 10 | 15 | 2009-10-12 02:17 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 3
2009-10-12 02:18 | 60.006 | 3679.5166 | 350 | -255.4442 | 0 |  | 10 | 15 | -103 | 7554.78 | 0 | 0 | 0 | -0.0029984 | 0.0029984 |  | 350 | -331.853 | 0 | 83 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 4
2009-10-12 02:18 | 60.006 | 3679.8879 | 350 | -255.4442 | 0 |  | 10 | 15 | -103 | 7555.11 | 0 | 0 | 0 | 0 | 0 |  | 350 | -331.853 | 0 | 83.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 5
2009-10-12 02:18 | 60.009 | 3679.6082 | 350 | -255.4442 | 0 |  | 10 | 15 | -103 | 7555.44 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -329.9882 | 0 | 84 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 6
2009-10-12 02:18 | 60.009 | 3679.0596 | 350 | -255.4442 | 0 |  | 10 | 15 | -103 | 7555.77 | 0 | 0 | 0 | 0 | 0 |  | 350 | -329.9882 | 0 | 84.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18
2009-10-12 02:18 | 60.008 | 3679.2607 | 350 | -254.8383 | 0 |  | 10 | 15 | -103 | 7556.1 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -329.9882 | 0 | 85 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18
2009-10-12 02:18 | 60.009 | 3679.1641 | 350 | -254.8383 | 0 |  | 10 | 15 | -103 | 7556.43 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -329.9882 | 0 | 85.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18
2009-10-12 02:18 | 60.009 | 3679.0247 | 350 | -254.8383 | 0 |  | 10 | 15 | -103 | 7556.76 | 0 | 0 | 0 | 0 | 0 |  | 350 | -329.9882 | 0 | 86 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18
2009-10-12 02:18 | 60.005 | 3679.1521 | 350 | -254.8383 | 0 |  | 10 | 15 | -103 | 7557.09 | 0 | 0 | 0 | -0.0039978 | 0.0039978 |  | 350 | -255.4442 | 0 | 86.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18
2009-10-12 02:18 | 60.004 | 3678.5723 | 350 | -254.8383 | 0 |  | 10 | 15 | -103 | 7557.42 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -255.4442 | 0 | 87 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:19
2009-10-12 02:18 | 60.001 | 3678.2952 | 350 | -257.147 | 0 |  | 10 | 15 | -103 | 7557.75 | 0 | 0 | 0 | -0.0030022 | 0.0030022 |  | 350 | -255.4442 | 0 | 87.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:19
2009-10-12 02:18 | 59.999 | 3678.2488 | 350 | -257.147 | 0 |  | 10 | 15 | -103 | 7558.08 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -255.4442 | 0 | 88 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19
2009-10-12 02:18 | 59.993 | 3678.2358 | 350 | -257.147 | 0 |  | 10 | 15 | -103 | 7558.41 | 0 | 0 | 0 | -0.0060005 | 0.0060005 |  | 350 | -255.4442 | 0 | 88.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19
2009-10-12 02:18 | 59.991 | 3677.8296 | 350 | -257.147 | 0 |  | 10 | 15 | -103 | 7558.74 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -254.8383 | 0 | 89 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19
2009-10-12 02:18 | 59.994 | 3677.9548 | 350 | -257.147 | 0 |  | 10 | 15 | -103 | 7559.07 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -254.8383 | 0 | 89.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:19
2009-10-12 02:18 | 59.992 | 3677.7722 | 350 | -262.2894 | 0 |  | 10 | 15 | -103 | 7559.4 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -254.8383 | 0 | 90 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:19
2009-10-12 02:18 | 59.994 | 3676.6658 | 350 | -262.2894 | 0 |  | 10 | 15 | -103 | 7559.73 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -254.8383 | 0 | 90.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:19
2009-10-12 02:18 | 59.992 | 3677.0933 | 350 | -262.2894 | 0 |  | 10 | 15 | -103 | 7560.06 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -254.8383 | 0 | 91 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:19
2009-10-12 02:18 | 59.994 | 3677.1406 | 350 | -262.2894 | 0 |  | 10 | 15 | -103 | 7560.39 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -257.147 | 0 | 91.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:19
2009-10-12 02:18 | 59.995 | 3676.4006 | 350 | -262.2894 | 0 |  | 10 | 15 | -103 | 7560.72 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -257.147 | 0 | 92 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20
2009-10-12 02:18 | 59.993 | 3678.5156 | 350 | -256.6479 | 0 |  | 10 | 15 | -103 | 7561.05 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -257.147 | 0 | 92.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20
2009-10-12 02:18 | 59.99 | 3679.8721 | 350 | -256.6479 | 0 |  | 10 | 15 | -103 | 7561.38 | 0 | 0 | 0 | -0.0029984 | 0.0029984 |  | 350 | -257.147 | 0 | 93 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20
2009-10-12 02:18 | 59.99 | 3680.1965 | 350 | -256.6479 | 0 |  | 10 | 15 | -103 | 7561.71 | 0 | 0 | 0 | 0 | 0 |  | 350 | -257.147 | 0 | 93.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20
2009-10-12 02:18 | 59.987 | 3678.7432 | 350 | -256.6479 | 0 |  | 10 | 15 | -103 | 7562.04 | 0 | 0 | 0 | -0.0030022 | 0.0030022 |  | 350 | -262.2894 | 0 | 94 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20
2009-10-12 02:18 | 59.983 | 3678.428 | 350 | -256.6479 | 0 |  | 10 | 15 | -103 | 7562.37 | 0 | 0 | 0 | -0.0039978 | 0.0039978 |  | 350 | -262.2894 | 0 | 94.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20
2009-10-12 02:18 | 59.977 | 3677.9211 | 350 | -256.3073 | 0 |  | 10 | 15 | -103 | 7562.7 | 0 | 0 | 0 | -0.0060005 | 0.0060005 |  | 350 | -262.2894 | 0 | 95 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20
2009-10-12 02:18 | 59.977 | 3680.2537 | 350 | -256.3073 | 0 |  | 10 | 15 | -103 | 7563.03 | 0 | 0 | 0 | 0 | 0 |  | 350 | -262.2894 | 0 | 95.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20
2009-10-12 02:18 | 59.989 | 3682.0701 | 350 | -256.3073 | 0 |  | 10 | 15 | -103 | 7563.36 | 0 | 0 | 0 | 0.011997 | 0.011997 |  | 350 | -262.2894 | 0 | 96 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20
2009-10-12 02:18 | 59.995 | 3681.3293 | 350 | -256.3073 | 0 |  | 10 | 15 | -103 | 7563.69 | 0 | 0 | 0 | 0.0060005 | 0.0060005 |  | 350 | -256.6479 | 0 | 96.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20
2009-10-12 02:18 | 59.999 | 3678.6555 | 350 | -256.3073 | 0 |  | 10 | 15 | -103 | 7564.02 | 0 | 0 | 0 | 0.0040016 | 0.0040016 |  | 350 | -256.6479 | 0 | 97 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20 | 2009-10-12 02:21
2009-10-12 02:18 | 59.994 | 3678.0767 | 350 | -249.0864 | 0 |  | 10 | 15 | -103 | 7564.35 | 0 | 0 | 0 | -0.0050011 | 0.0050011 |  | 350 | -256.6479 | 0 | 97.5 | 10 | 15 | 2009-10-12 02:18 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20 | 2009-10-12 02:21
2009-10-12 02:19 | 59.989 | 3677.78 | 350 | -249.0864 | 0 |  | 10 | 15 | -103 | 7564.68 | 0 | 0 | 0 | -0.0050011 | 0.0050011 |  | 350 | -256.6479 | 0 | 98 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20 | 2009-10-12 02:21
2009-10-12 02:19 | 59.987 | 3678.4268 | 350 | -249.0864 | 0 |  | 10 | 15 | -103 | 7565.01 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -256.6479 | 0 | 98.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20 | 2009-10-12 02:21
2009-10-12 02:19 | 59.986 | 3678.4731 | 350 | -249.0864 | 0 |  | 10 | 15 | -103 | 7565.34 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -256.3073 | 0 | 99 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20 | 2009-10-12 02:21
2009-10-12 02:19 | 59.984 | 3678.2778 | 350 | -249.0864 | 0 |  | 10 | 15 | -103 | 7565.67 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -256.3073 | 0 | 99.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20 | 2009-10-12 02:21
2009-10-12 02:19 | 59.983 | 3677.8223 | 350 | -253.7425 | 0 |  | 10 | 15 | -103 | 7566 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -256.3073 | 0 | 100 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:21
2009-10-12 02:19 | 59.985 | 3676.615 | 350 | -253.7425 | 0 |  | 10 | 15 | -103 | 7566.33 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -256.3073 | 0 | 100.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:21
2009-10-12 02:19 | 59.986 | 3677.3975 | 350 | -253.7425 | 0 |  | 10 | 15 | -103 | 7566.66 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -256.3073 | 0 | 101 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:21
2009-10-12 02:19 | 59.985 | 3677.917 | 350 | -253.7425 | 0 |  | 10 | 15 | -103 | 7566.99 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -249.0864 | 0 | 101.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:21
2009-10-12 02:19 | 59.986 | 3677.9497 | 350 | -253.7425 | 0 |  | 10 | 15 | -103 | 7567.32 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -249.0864 | 0 | 102 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22
2009-10-12 02:19 | 59.98 | 3678.6167 | 350 | -257.4212 | 0 |  | 10 | 15 | -103 | 7567.65 | 0 | 0 | 0 | -0.0060005 | 0.0060005 |  | 350 | -249.0864 | 0 | 102.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22
2009-10-12 02:19 | 59.981 | 3678.9626 | 350 | -257.4212 | 0 |  | 10 | 15 | -103 | 7567.98 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -249.0864 | 0 | 103 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22
2009-10-12 02:19 | 59.981 | 3681.2522 | 350 | -257.4212 | 0 |  | 10 | 15 | -103 | 7568.31 | 0 | 0 | 0 | 0 | 0 |  | 350 | -249.0864 | 0 | 103.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22
2009-10-12 02:19 | 59.989 | 3680.7373 | 350 | -257.4212 | 0 |  | 10 | 15 | -103 | 7568.64 | 0 | 0 | 0 | 0.0079994 | 0.0079994 |  | 350 | -253.7425 | 0 | 104 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22
2009-10-12 02:19 | 59.998 | 3680.0449 | 350 | -257.4212 | 0 |  | 10 | 15 | -103 | 7568.97 | 0 | 0 | 0 | 0.0090027 | 0.0090027 |  | 350 | -253.7425 | 0 | 104.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:21 | 2009-10-12 02:22
2009-10-12 02:19 | 60.007 | 3678.1614 | 350 | -261.7382 | 0 |  | 10 | 15 | -103 | 7569.3 | 0 | 0 | 0 | 0.0089989 | 0.0089989 |  | 350 | -253.7425 | 0 | 105 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:21 | 2009-10-12 02:22
2009-10-12 02:19 | 60.007 | 3674.0762 | 350 | -261.7382 | 0 |  | 10 | 15 | -103 | 7569.63 | 0 | 0 | 0 | 0 | 0 |  | 350 | -253.7425 | 0 | 105.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:21 | 2009-10-12 02:22
2009-10-12 02:19 | 59.997 | 3676.2222 | 350 | -261.7382 | 0 |  | 10 | 15 | -103 | 7569.96 | 0 | 0 | 0 | -0.0099983 | 0.0099983 |  | 350 | -253.7425 | 0 | 106 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:22
2009-10-12 02:19 | 59.986 | 3676.6694 | 350 | -261.7382 | 0 |  | 10 | 15 | -103 | 7570.29 | 0 | 0 | 0 | -0.011002 | 0.011002 |  | 350 | -257.4212 | 0 | 106.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:22
2009-10-12 02:19 | 59.981 | 3677.4971 | 350 | -261.7382 | 0 |  | 10 | 15 | -103 | 7570.62 | 0 | 0 | 0 | -0.0050011 | 0.0050011 |  | 350 | -257.4212 | 0 | 107 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23
2009-10-12 02:19 | 59.977 | 3677.49 | 350 | -271.876 | 0 |  | 10 | 15 | -103 | 7570.95 | 0 | 0 | 0 | -0.0039978 | 0.0039978 |  | 350 | -257.4212 | 0 | 107.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23
2009-10-12 02:19 | 59.974 | 3675.1858 | 350 | -271.876 | 0 |  | 10 | 15 | -103 | 7571.28 | 0 | 0 | 0 | -0.0030022 | 0.0030022 |  | 350 | -257.4212 | 0 | 108 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23
2009-10-12 02:19 | 59.976 | 3675.437 | 350 | -271.876 | 0 |  | 10 | 15 | -103 | 7571.61 | 0 | 0 | 0 | 0.0020027 | 0.0020027 |  | 350 | -257.4212 | 0 | 108.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23
2009-10-12 02:19 | 59.974 | 3680.4509 | 350 | -271.876 | 0 |  | 10 | 15 | -103 | 7571.94 | 0 | 0 | 0 | -0.0020027 | 0.0020027 |  | 350 | -261.7382 | 0 | 109 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23
2009-10-12 02:19 | 59.974 | 3682.0317 | 350 | -271.876 | 0 |  | 10 | 15 | -103 | 7572.27 | 0 | 0 | 0 | 0 | 0 |  | 350 | -261.7382 | 0 | 109.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23
2009-10-12 02:19 | 59.977 | 3683.8286 | 350 | -262.0735 | 0 |  | 10 | 15 | -103 | 7572.6 | 0 | 0 | 0 | 0.0030022 | 0.0030022 |  | 350 | -261.7382 | 0 | 110 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23
2009-10-12 02:19 | 59.979 | 3682.8433 | 350 | -262.0735 | 0 |  | 10 | 15 | -103 | 7572.93 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -261.7382 | 0 | 110.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23
2009-10-12 02:19 | 59.979 | 3681.1084 | 350 | -262.0735 | 0 |  | 10 | 15 | -103 | 7573.26 | 0 | 0 | 0 | 0 | 0 |  | 350 | -261.7382 | 0 | 111 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23
2009-10-12 02:19 | 59.982 | 3680.5657 | 350 | -262.0735 | 0 |  | 10 | 15 | -103 | 7573.59 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -271.876 | 0 | 111.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23
2009-10-12 02:19 | 59.984 | 3678.229 | 350 | -262.0735 | 0 |  | 10 | 15 | -103 | 7573.92 | 0 | 0 | 0 | 0.0020027 | 0.0020027 |  | 350 | -271.876 | 0 | 112 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24
2009-10-12 02:19 | 59.987 | 3676.752 | 350 | -260.3644 | 0 |  | 10 | 15 | -103 | 7574.25 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -271.876 | 0 | 112.5 | 10 | 15 | 2009-10-12 02:19 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24
2009-10-12 02:20 | 59.988 | 3675.7593 | 350 | -260.3644 | 0 |  | 10 | 15 | -103 | 7574.58 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -271.876 | 0 | 113 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24
2009-10-12 02:20 | 59.988 | 3671.9424 | 350 | -260.3644 | 0 |  | 10 | 15 | -103 | 7574.91 | 0 | 0 | 0 | 0 | 0 |  | 350 | -271.876 | 0 | 113.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24
2009-10-12 02:20 | 59.987 | 3671.1655 | 350 | -260.3644 | 0 |  | 10 | 15 | -103 | 7575.24 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -262.0735 | 0 | 114 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24
2009-10-12 02:20 | 59.987 | 3670.4758 | 350 | -260.3644 | 0 |  | 10 | 15 | -103 | 7575.57 | 0 | 0 | 0 | 0 | 0 |  | 350 | -262.0735 | 0 | 114.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24
2009-10-12 02:20 | 59.987 | 3670.1287 | 350 | -352.6444 | 0 |  | 10 | 15 | -103 | 7575.9 | 0 | 0 | 0 | 0 | 0 |  | 350 | -262.0735 | 0 | 115 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24
2009-10-12 02:20 | 59.985 | 3671.5415 | 350 | -352.6444 | 0 |  | 10 | 15 | -103 | 7576.23 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -262.0735 | 0 | 115.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24
2009-10-12 02:20 | 59.984 | 3672.0479 | 350 | -352.6444 | 0 |  | 10 | 15 | -103 | 7576.56 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -262.0735 | 0 | 116 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24
2009-10-12 02:20 | 59.982 | 3671.5757 | 350 | -352.6444 | 0 |  | 10 | 15 | -103 | 7576.89 | 0 | 0 | 0 | -0.0020027 | 0.0020027 |  | 350 | -260.3644 | 0 | 116.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24
2009-10-12 02:20 | 59.983 | 3672.1035 | 350 | -352.6444 | 0 |  | 10 | 15 | -103 | 7577.22 | 0 | 0 | 0 | 0.0010033 | 0.0010033 |  | 350 | -260.3644 | 0 | 117 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:25
2009-10-12 02:20 | 59.989 | 3672.4136 | 350 | -354.8957 | 0 |  | 10 | 15 | -103 | 7577.55 | 0 | 0 | 0 | 0.0059967 | 0.0059967 |  | 350 | -260.3644 | 0 | 117.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:25
2009-10-12 02:20 | 59.989 | 3671.8823 | 350 | -354.8957 | 0 |  | 10 | 15 | -103 | 7577.88 | 0 | 0 | 0 | 0 | 0 |  | 350 | -260.3644 | 0 | 118 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:25
2009-10-12 02:20 | 59.988 | 3671.8372 | 350 | -354.8957 | 0 |  | 10 | 15 | -103 | 7578.21 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -260.3644 | 0 | 118.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:25
2009-10-12 02:20 | 59.984 | 3671.3359 | 350 | -354.8957 | 0 |  | 10 | 15 | -103 | 7578.54 | 0 | 0 | 0 | -0.0039978 | 0.0039978 |  | 350 | -352.6444 | 0 | 119 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:25
2009-10-12 02:20 | 59.982 | 3670.7258 | 350 | -354.8957 | 0 |  | 10 | 15 | -103 | 7578.87 | 0 | 0 | 0 | -0.0020027 | 0.0020027 |  | 350 | -352.6444 | 0 | 119.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:25
2009-10-12 02:20 | 59.983 | 3670.3721 | 350 | -340.4694 | 0 |  | 10 | 15 | -103 | 7579.2 | 0 | 0 | 0 | 0.0010033 | 0.0010033 |  | 350 | -352.6444 | 0 | 120 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:25
2009-10-12 02:20 | 59.981 | 3671.364 | 350 | -340.4694 | 0 |  | 10 | 15 | -103 | 7579.53 | 0 | 0 | 0 | -0.0020027 | 0.0020027 |  | 350 | -352.6444 | 0 | 120.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:25
2009-10-12 02:20 | 59.982 | 3671.4009 | 350 | -340.4694 | 0 |  | 10 | 15 | -103 | 7579.86 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -352.6444 | 0 | 121 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:25
2009-10-12 02:20 | 59.983 | 3672.1562 | 350 | -340.4694 | 0 |  | 10 | 15 | -103 | 7580.19 | 0 | 0 | 0 | 0.0010033 | 0.0010033 |  | 350 | -354.8957 | 0 | 121.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:25
2009-10-12 02:20 | 59.986 | 3672.1814 | 350 | -340.4694 | 0 |  | 10 | 15 | -103 | 7580.52 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -354.8957 | 0 | 122 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:26
2009-10-12 02:20 | 59.989 | 3670.2964 | 350 | -337.6429 | 0 |  | 10 | 15 | -103 | 7580.85 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -354.8957 | 0 | 122.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:26
2009-10-12 02:20 | 59.987 | 3668.0708 | 350 | -337.6429 | 0 |  | 10 | 15 | -103 | 7581.18 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -354.8957 | 0 | 123 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:26
2009-10-12 02:20 | 59.985 | 3668.5896 | 350 | -337.6429 | 0 |  | 10 | 15 | -103 | 7581.51 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -354.8957 | 0 | 123.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:26
2009-10-12 02:20 | 59.98 | 3669.9082 | 350 | -337.6429 | 0 |  | 10 | 15 | -103 | 7581.84 | 0 | 0 | 0 | -0.0050011 | 0.0050011 |  | 350 | -340.4694 | 0 | 124 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:26
2009-10-12 02:20 | 59.98 | 3670.3994 | 350 | -337.6429 | 0 |  | 10 | 15 | -103 | 7582.17 | 0 | 0 | 0 | 0 | 0 |  | 350 | -340.4694 | 0 | 124.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:26
2009-10-12 02:20 | 59.983 | 3670.2627 | 350 | -284.3608 | 0 |  | 10 | 15 | -103 | 7582.5 | 0 | 0 | 0 | 0.0030022 | 0.0030022 |  | 350 | -340.4694 | 0 | 125 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:26
2009-10-12 02:20 | 59.98 | 3669.3823 | 350 | -284.3608 | 0 |  | 10 | 15 | -103 | 7582.83 | 0 | 0 | 0 | -0.0030022 | 0.0030022 |  | 350 | -340.4694 | 0 | 125.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:26
2009-10-12 02:20 | 59.979 | 3670.1021 | 350 | -284.3608 | 0 |  | 10 | 15 | -103 | 7583.16 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -340.4694 | 0 | 126 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:26
2009-10-12 02:20 | 59.979 | 3670.4375 | 350 | -284.3608 | 0 |  | 10 | 15 | -103 | 7583.49 | 0 | 0 | 0 | 0 | 0 |  | 350 | -337.6429 | 0 | 126.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:26
2009-10-12 02:20 | 59.981 | 3671.4026 | 350 | -284.3608 | 0 |  | 10 | 15 | -103 | 7583.82 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -337.6429 | 0 | 127 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:25 | 2009-10-12 02:27
2009-10-12 02:20 | 59.981 | 3672.4424 | 350 | -260.468 | 0 |  | 10 | 15 | -103 | 7584.15 | 0 | 0 | 0 | 0 | 0 |  | 350 | -337.6429 | 0 | 127.5 | 10 | 15 | 2009-10-12 02:20 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:25 | 2009-10-12 02:27
2009-10-12 02:21 | 59.98 | 3672.3718 | 350 | -260.468 | 0 |  | 10 | 15 | -103 | 7584.48 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -337.6429 | 0 | 128 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:25 | 2009-10-12 02:27
2009-10-12 02:21 | 59.98 | 3671.947 | 350 | -260.468 | 0 |  | 10 | 15 | -103 | 7584.81 | 0 | 0 | 0 | 0 | 0 |  | 350 | -337.6429 | 0 | 128.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:25 | 2009-10-12 02:27
2009-10-12 02:21 | 59.981 | 3670.9375 | 350 | -260.468 | 0 |  | 10 | 15 | -103 | 7585.14 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -284.3608 | 0 | 129 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:25 | 2009-10-12 02:27
2009-10-12 02:21 | 59.98 | 3670.7046 | 350 | -260.468 | 0 |  | 10 | 15 | -103 | 7585.47 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -284.3608 | 0 | 129.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:25 | 2009-10-12 02:27
2009-10-12 02:21 | 59.98 | 3670.1372 | 350 | -253.1415 | 0 |  | 10 | 15 | -103 | 7585.8 | 0 | 0 | 0 | 0 | 0 |  | 350 | -284.3608 | 0 | 130 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:27
2009-10-12 02:21 | 59.977 | 3669.2793 | 350 | -253.1415 | 0 |  | 10 | 15 | -103 | 7586.13 | 0 | 0 | 0 | -0.0029984 | 0.0029984 |  | 350 | -284.3608 | 0 | 130.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:27
2009-10-12 02:21 | 59.979 | 3672.3909 | 350 | -253.1415 | 0 |  | 10 | 15 | -103 | 7586.46 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -284.3608 | 0 | 131 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:27
2009-10-12 02:21 | 59.981 | 3672.5579 | 350 | -253.1415 | 0 |  | 10 | 15 | -103 | 7586.79 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -260.468 | 0 | 131.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:27
2009-10-12 02:21 | 59.979 | 3674.0518 | 350 | -253.1415 | 0 |  | 10 | 15 | -103 | 7587.12 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -260.468 | 0 | 132 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28
2009-10-12 02:21 | 59.976 | 3672.6265 | 350 | -251.9299 | 0 |  | 10 | 15 | -103 | 7587.45 | 0 | 0 | 0 | -0.0029984 | 0.0029984 |  | 350 | -260.468 | 0 | 132.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28
2009-10-12 02:21 | 59.977 | 3671.8003 | 350 | -251.9299 | 0 |  | 10 | 15 | -103 | 7587.78 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -260.468 | 0 | 133 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28
2009-10-12 02:21 | 59.972 | 3673.1829 | 350 | -251.9299 | 0 |  | 10 | 15 | -103 | 7588.11 | 0 | 0 | 0 | -0.0050011 | 0.0050011 |  | 350 | -260.468 | 0 | 133.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28
2009-10-12 02:21 | 59.971 | 3673.8735 | 350 | -251.9299 | 0 |  | 10 | 15 | -103 | 7588.44 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -253.1415 | 0 | 134 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28
2009-10-12 02:21 | 59.973 | 3676.2627 | 350 | -251.9299 | 0 |  | 10 | 15 | -103 | 7588.77 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -253.1415 | 0 | 134.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:26 | 2009-10-12 02:28
2009-10-12 02:21 | 59.973 | 3676.6233 | 350 | -250.6742 | 0 |  | 10 | 15 | -103 | 7589.1 | 0 | 0 | 0 | 0 | 0 |  | 350 | -253.1415 | 0 | 135 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:26 | 2009-10-12 02:28
2009-10-12 02:21 | 59.973 | 3676.8699 | 350 | -250.6742 | 0 |  | 10 | 15 | -103 | 7589.43 | 0 | 0 | 0 | 0 | 0 |  | 350 | -253.1415 | 0 | 135.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:26 | 2009-10-12 02:28
2009-10-12 02:21 | 59.974 | 3676.543 | 350 | -250.6742 | 0 |  | 10 | 15 | -103 | 7589.76 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -253.1415 | 0 | 136 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:28
2009-10-12 02:21 | 59.971 | 3675.4641 | 350 | -250.6742 | 0 |  | 10 | 15 | -103 | 7590.09 | 0 | 0 | 0 | -0.0029984 | 0.0029984 |  | 350 | -251.9299 | 0 | 136.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:28
2009-10-12 02:21 | 59.975 | 3675.7524 | 350 | -250.6742 | 0 |  | 10 | 15 | -103 | 7590.42 | 0 | 0 | 0 | 0.0039978 | 0.0039978 |  | 350 | -251.9299 | 0 | 137 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29
2009-10-12 02:21 | 59.977 | 3675.2559 | 350 | -253.6319 | 0 |  | 10 | 15 | -103 | 7590.75 | 0 | 0 | 0 | 0.0020027 | 0.0020027 |  | 350 | -251.9299 | 0 | 137.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29
2009-10-12 02:21 | 59.977 | 3674.8696 | 350 | -253.6319 | 0 |  | 10 | 15 | -103 | 7591.08 | 0 | 0 | 0 | 0 | 0 |  | 350 | -251.9299 | 0 | 138 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29
2009-10-12 02:21 | 59.975 | 3671.2769 | 350 | -253.6319 | 0 |  | 10 | 15 | -103 | 7591.41 | 0 | 0 | 0 | -0.0020027 | 0.0020027 |  | 350 | -251.9299 | 0 | 138.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29
2009-10-12 02:21 | 59.976 | 3671.5933 | 350 | -253.6319 | 0 |  | 10 | 15 | -103 | 7591.74 | 0 | 0 | 0 | 0.0010033 | 0.0010033 |  | 350 | -250.6742 | 0 | 139 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29
2009-10-12 02:21 | 59.98 | 3670.5869 | 350 | -253.6319 | 0 |  | 10 | 15 | -103 | 7592.07 | 0 | 0 | 0 | 0.0039978 | 0.0039978 |  | 350 | -250.6742 | 0 | 139.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29
2009-10-12 02:21 | 59.979 | 3669.9629 | 350 | -246.9573 | 0 |  | 10 | 15 | -103 | 7592.4 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -250.6742 | 0 | 140 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29
2009-10-12 02:21 | 59.981 | 3669.54 | 350 | -246.9573 | 0 |  | 10 | 15 | -103 | 7592.73 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -250.6742 | 0 | 140.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29
2009-10-12 02:21 | 59.982 | 3669.4968 | 350 | -246.9573 | 0 |  | 10 | 15 | -103 | 7593.06 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -250.6742 | 0 | 141 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29
2009-10-12 02:21 | 59.982 | 3668.7056 | 350 | -246.9573 | 0 |  | 10 | 15 | -103 | 7593.39 | 0 | 0 | 0 | 0 | 0 |  | 350 | -253.6319 | 0 | 141.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29
2009-10-12 02:21 | 59.982 | 3667.6765 | 350 | -246.9573 | 0 |  | 10 | 15 | -103 | 7593.72 | 0 | 0 | 0 | 0 | 0 |  | 350 | -253.6319 | 0 | 142 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:30
2009-10-12 02:21 | 59.982 | 3666.4817 | 350 | -254.5418 | 0 |  | 10 | 15 | -103 | 7594.05 | 0 | 0 | 0 | 0 | 0 |  | 350 | -253.6319 | 0 | 142.5 | 10 | 15 | 2009-10-12 02:21 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:30
2009-10-12 02:22 | 59.981 | 3666.5994 | 350 | -254.5418 | 0 |  | 10 | 15 | -103 | 7594.38 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -253.6319 | 0 | 143 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:30
2009-10-12 02:22 | 59.982 | 3666.9106 | 350 | -254.5418 | 0 |  | 10 | 15 | -103 | 7594.71 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -253.6319 | 0 | 143.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:30
2009-10-12 02:22 | 59.984 | 3666.4417 | 350 | -254.5418 | 0 |  | 10 | 15 | -103 | 7595.04 | 0 | 0 | 0 | 0.0020027 | 0.0020027 |  | 350 | -246.9573 | 0 | 144 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:30
2009-10-12 02:22 | 59.985 | 3666.4048 | 350 | -254.5418 | 0 |  | 10 | 15 | -103 | 7595.37 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -246.9573 | 0 | 144.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:30
2009-10-12 02:22 | 59.987 | 3667.4563 | 350 | -256.5716 | 0 |  | 10 | 15 | -103 | 7595.7 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -246.9573 | 0 | 145 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:30
2009-10-12 02:22 | 59.989 | 3666.3804 | 350 | -256.5716 | 0 |  | 10 | 15 | -103 | 7596.03 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -246.9573 | 0 | 145.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:30
2009-10-12 02:22 | 59.993 | 3665.2617 | 350 | -256.5716 | 0 |  | 10 | 15 | -103 | 7596.36 | 0 | 0 | 0 | 0.0040016 | 0.0040016 |  | 350 | -246.9573 | 0 | 146 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:30
2009-10-12 02:22 | 59.996 | 3664.031 | 350 | -256.5716 | 0 |  | 10 | 15 | -103 | 7596.69 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -254.5418 | 0 | 146.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:30
2009-10-12 02:22 | 59.998 | 3663.825 | 350 | -256.5716 | 0 |  | 10 | 15 | -103 | 7597.02 | 0 | 0 | 0 | 0.0020027 | 0.0020027 |  | 350 | -254.5418 | 0 | 147 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:31
2009-10-12 02:22 | 59.998 | 3663.2288 | 350 | -258.3726 | 0 |  | 10 | 15 | -103 | 7597.35 | 0 | 0 | 0 | 0 | 0 |  | 350 | -254.5418 | 0 | 147.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:31
2009-10-12 02:22 | 60.004 | 3662.0549 | 350 | -258.3726 | 0 |  | 10 | 15 | -103 | 7597.68 | 0 | 0 | 0 | 0.0060005 | 0.0060005 |  | 350 | -254.5418 | 0 | 148 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:31
2009-10-12 02:22 | 60.007 | 3661.6953 | 350 | -258.3726 | 0 |  | 10 | 15 | -103 | 7598.01 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -254.5418 | 0 | 148.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:31
2009-10-12 02:22 | 60.01 | 3662.0762 | 350 | -258.3726 | 0 |  | 10 | 15 | -103 | 7598.34 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -256.5716 | 0 | 149 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:31
2009-10-12 02:22 | 60.013 | 3662.2239 | 350 | -258.3726 | 0 |  | 10 | 15 | -103 | 7598.67 | 0 | 0 | 0 | 0.0030022 | 0.0030022 |  | 350 | -256.5716 | 0 | 149.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:29 | 2009-10-12 02:31
2009-10-12 02:22 | 60.014 | 3662.9595 | 350 | -263.0474 | 0 |  | 10 | 15 | -103 | 7599 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -256.5716 | 0 | 150 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:29 | 2009-10-12 02:31
2009-10-12 02:22 | 60.013 | 3663.7944 | 350 | -263.0474 | 0 |  | 10 | 15 | -103 | 7599.33 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -256.5716 | 0 | 150.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:29 | 2009-10-12 02:31
2009-10-12 02:22 | 60.008 | 3664.1392 | 350 | -263.0474 | 0 |  | 10 | 15 | -103 | 7599.66 | 0 | 0 | 0 | -0.0050011 | 0.0050011 |  | 350 | -256.5716 | 0 | 151 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:29 | 2009-10-12 02:31
2009-10-12 02:22 | 60.008 | 3665.2778 | 350 | -263.0474 | 0 |  | 10 | 15 | -103 | 7599.99 | 0 | 0 | 0 | 0 | 0 |  | 350 | -258.3726 | 0 | 151.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:29 | 2009-10-12 02:31
2009-10-12 02:22 | 60.01 | 3664.1587 | 350 | -263.0474 | 0 |  | 10 | 15 | -103 | 7600.32 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -258.3726 | 0 | 152 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:29 | 2009-10-12 02:32
2009-10-12 02:22 | 60.019 | 3663.2646 | 350 | -260.9844 | 0 |  | 10 | 15 | -103 | 7600.65 | 0 | 0 | 0 | 0.0090027 | 0.0090027 |  | 350 | -258.3726 | 0 | 152.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29 | 2009-10-12 02:32
2009-10-12 02:22 | 60.019 | 3663.1836 | 350 | -260.9844 | 0 |  | 10 | 15 | -103 | 7600.98 | 0 | 0 | 0 | 0 | 0 |  | 350 | -258.3726 | 0 | 153 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29 | 2009-10-12 02:32
2009-10-12 02:22 | 60.023 | 3661.9292 | 350 | -260.9844 | 0 |  | 10 | 15 | -103 | 7601.31 | 0 | 0 | 0 | 0.0039978 | 0.0039978 |  | 350 | -258.3726 | 0 | 153.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:29 | 2009-10-12 02:32
2009-10-12 02:22 | 60.021 | 3661.5122 | 350 | -260.9844 | 0 |  | 10 | 15 | -103 | 7601.64 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -263.0474 | 0 | 154 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:32
2009-10-12 02:22 | 60.02 | 3659.1724 | 350 | -260.9844 | 0 |  | 10 | 15 | -103 | 7601.97 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -263.0474 | 0 | 154.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:32
2009-10-12 02:22 | 60.021 | 3658.6614 | 350 | -261.3183 | 0 |  | 10 | 15 | -103 | 7602.3 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -263.0474 | 0 | 155 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:32
2009-10-12 02:22 | 60.021 | 3656.7854 | 350 | -261.3183 | 0 |  | 10 | 15 | -103 | 7602.63 | 0 | 0 | 0 | 0 | 0 |  | 350 | -263.0474 | 0 | 155.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:32
2009-10-12 02:22 | 60.02 | 3657.571 | 350 | -261.3183 | 0 |  | 10 | 15 | -103 | 7602.96 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -263.0474 | 0 | 156 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:32
2009-10-12 02:22 | 60.019 | 3658.126 | 350 | -261.3183 | 0 |  | 10 | 15 | -103 | 7603.29 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -260.9844 | 0 | 156.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:25 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:32
2009-10-12 02:22 | 60.019 | 3657.7104 | 350 | -261.3183 | 0 |  | 10 | 15 | -103 | 7603.62 | 0 | 0 | 0 | 0 | 0 |  | 350 | -260.9844 | 0 | 157 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:30 | 2009-10-12 02:33
2009-10-12 02:22 | 60.022 | 3658.0146 | 350 | -262.1026 | 0 |  | 10 | 15 | -103 | 7603.95 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -260.9844 | 0 | 157.5 | 10 | 15 | 2009-10-12 02:22 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:30 | 2009-10-12 02:33
2009-10-12 02:23 | 60.025 | 3660.2275 | 350 | -262.1026 | 0 |  | 10 | 15 | -103 | 7604.28 | 0 | 0 | 0 | 0.0030022 | 0.0030022 |  | 350 | -260.9844 | 0 | 158 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:30 | 2009-10-12 02:33
2009-10-12 02:23 | 60.025 | 3659.2236 | 350 | -262.1026 | 0 |  | 10 | 15 | -103 | 7604.61 | 0 | 0 | 0 | 0 | 0 |  | 350 | -260.9844 | 0 | 158.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:30 | 2009-10-12 02:33
2009-10-12 02:23 | 60.026 | 3658.6982 | 350 | -262.1026 | 0 |  | 10 | 15 | -103 | 7604.94 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -261.3183 | 0 | 159 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:30 | 2009-10-12 02:33
2009-10-12 02:23 | 60.02 | 3658.6687 | 350 | -262.1026 | 0 |  | 10 | 15 | -103 | 7605.27 | 0 | 0 | 0 | -0.0060005 | 0.0060005 |  | 350 | -261.3183 | 0 | 159.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:30 | 2009-10-12 02:33
2009-10-12 02:23 | 60.02 | 3658.1545 | 350 | -262.717 | 0 |  | 10 | 15 | -103 | 7605.6 | 0 | 0 | 0 | 0 | 0 |  | 350 | -261.3183 | 0 | 160 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:33
2009-10-12 02:23 | 60.018 | 3659.1296 | 350 | -262.717 | 0 |  | 10 | 15 | -103 | 7605.93 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -261.3183 | 0 | 160.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:33
2009-10-12 02:23 | 60.018 | 3659.7776 | 350 | -262.717 | 0 |  | 10 | 15 | -103 | 7606.26 | 0 | 0 | 0 | 0 | 0 |  | 350 | -261.3183 | 0 | 161 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:33
2009-10-12 02:23 | 60.02 | 3660.8196 | 350 | -262.717 | 0 |  | 10 | 15 | -103 | 7606.59 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -262.1026 | 0 | 161.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:33
2009-10-12 02:23 | 60.019 | 3662.5315 | 350 | -262.717 | 0 |  | 10 | 15 | -103 | 7606.92 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -262.1026 | 0 | 162 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:34
2009-10-12 02:23 | 60.019 | 3662.3872 | 350 | -260.0165 | 0 |  | 10 | 15 | -103 | 7607.25 | 0 | 0 | 0 | 0 | 0 |  | 350 | -262.1026 | 0 | 162.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:34
2009-10-12 02:23 | 60.023 | 3662.0789 | 350 | -260.0165 | 0 |  | 10 | 15 | -103 | 7607.58 | 0 | 0 | 0 | 0.0039978 | 0.0039978 |  | 350 | -262.1026 | 0 | 163 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:34
2009-10-12 02:23 | 60.022 | 3662.3901 | 350 | -260.0165 | 0 |  | 10 | 15 | -103 | 7607.91 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -262.1026 | 0 | 163.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:34
2009-10-12 02:23 | 60.022 | 3662.6782 | 350 | -260.0165 | 0 |  | 10 | 15 | -103 | 7608.24 | 0 | 0 | 0 | 0 | 0 |  | 350 | -262.717 | 0 | 164 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:34
2009-10-12 02:23 | 60.025 | 3663.5767 | 350 | -260.0165 | 0 |  | 10 | 15 | -103 | 7608.57 | 0 | 0 | 0 | 0.0030022 | 0.0030022 |  | 350 | -262.717 | 0 | 164.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:31 | 2009-10-12 02:34
2009-10-12 02:23 | 60.02 | 3663.5386 | 350 | -263.8732 | 0 |  | 10 | 15 | -103 | 7608.9 | 0 | 0 | 0 | -0.0050011 | 0.0050011 |  | 350 | -262.717 | 0 | 165 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:31 | 2009-10-12 02:34
2009-10-12 02:23 | 60.02 | 3662.9592 | 350 | -263.8732 | 0 |  | 10 | 15 | -103 | 7609.23 | 0 | 0 | 0 | 0 | 0 |  | 350 | -262.717 | 0 | 165.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:31 | 2009-10-12 02:34
2009-10-12 02:23 | 60.02 | 3662.5525 | 350 | -263.8732 | 0 |  | 10 | 15 | -103 | 7609.56 | 0 | 0 | 0 | 0 | 0 |  | 350 | -262.717 | 0 | 166 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:34
2009-10-12 02:23 | 60.02 | 3662.543 | 350 | -263.8732 | 0 |  | 10 | 15 | -103 | 7609.89 | 0 | 0 | 0 | 0 | 0 |  | 350 | -260.0165 | 0 | 166.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:34
2009-10-12 02:23 | 60.02 | 3663.6006 | 350 | -263.8732 | 0 |  | 10 | 15 | -103 | 7610.22 | 0 | 0 | 0 | 0 | 0 |  | 350 | -260.0165 | 0 | 167 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:35
2009-10-12 02:23 | 60.021 | 3663.9097 | 350 | -264.5979 | 0 |  | 10 | 15 | -103 | 7610.55 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -260.0165 | 0 | 167.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:35
2009-10-12 02:23 | 60.021 | 3663.6899 | 350 | -264.5979 | 0 |  | 10 | 15 | -103 | 7610.88 | 0 | 0 | 0 | 0 | 0 |  | 350 | -260.0165 | 0 | 168 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:35
2009-10-12 02:23 | 60.018 | 3662.7913 | 350 | -264.5979 | 0 |  | 10 | 15 | -103 | 7611.21 | 0 | 0 | 0 | -0.0029984 | 0.0029984 |  | 350 | -260.0165 | 0 | 168.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:35
2009-10-12 02:23 | 60.014 | 3663.3958 | 350 | -264.5979 | 0 |  | 10 | 15 | -103 | 7611.54 | 0 | 0 | 0 | -0.0040016 | 0.0040016 |  | 350 | -263.8732 | 0 | 169 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:35
2009-10-12 02:23 | 60.014 | 3663.6978 | 350 | -264.5979 | 0 |  | 10 | 15 | -103 | 7611.87 | 0 | 0 | 0 | 0 | 0 |  | 350 | -263.8732 | 0 | 169.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:35
2009-10-12 02:23 | 60.014 | 3664.3154 | 350 | -262.4159 | 0 |  | 10 | 15 | -103 | 7612.2 | 0 | 0 | 0 | 0 | 0 |  | 350 | -263.8732 | 0 | 170 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:35
2009-10-12 02:23 | 60.013 | 3665.313 | 350 | -262.4159 | 0 |  | 10 | 15 | -103 | 7612.53 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -263.8732 | 0 | 170.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:35
2009-10-12 02:23 | 60.013 | 3665.7976 | 350 | -262.4159 | 0 |  | 10 | 15 | -103 | 7612.86 | 0 | 0 | 0 | 0 | 0 |  | 350 | -263.8732 | 0 | 171 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:35
2009-10-12 02:23 | 60.01 | 3666.1411 | 350 | -262.4159 | 0 |  | 10 | 15 | -103 | 7613.19 | 0 | 0 | 0 | -0.0030022 | 0.0030022 |  | 350 | -264.5979 | 0 | 171.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:35
2009-10-12 02:23 | 60.008 | 3666.7258 | 350 | -262.4159 | 0 |  | 10 | 15 | -103 | 7613.52 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -264.5979 | 0 | 172 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:36
2009-10-12 02:23 | 60.011 | 3667.6768 | 350 | -259.6852 | 0 |  | 10 | 15 | -103 | 7613.85 | 0 | 0 | 0 | 0.0030022 | 0.0030022 |  | 350 | -264.5979 | 0 | 172.5 | 10 | 15 | 2009-10-12 02:23 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:36
2009-10-12 02:24 | 60.011 | 3667.5454 | 350 | -259.6852 | 0 |  | 10 | 15 | -103 | 7614.18 | 0 | 0 | 0 | 0 | 0 |  | 350 | -264.5979 | 0 | 173 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:36
2009-10-12 02:24 | 60.012 | 3666.6882 | 350 | -259.6852 | 0 |  | 10 | 15 | -103 | 7614.51 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -264.5979 | 0 | 173.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:36
2009-10-12 02:24 | 60.012 | 3666.4487 | 350 | -259.6852 | 0 |  | 10 | 15 | -103 | 7614.84 | 0 | 0 | 0 | 0 | 0 |  | 350 | -262.4159 | 0 | 174 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:36
2009-10-12 02:24 | 60.009 | 3666.7104 | 350 | -259.6852 | 0 |  | 10 | 15 | -103 | 7615.17 | 0 | 0 | 0 | -0.0030022 | 0.0030022 |  | 350 | -262.4159 | 0 | 174.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:36
2009-10-12 02:24 | 60.009 | 3667.696 | 350 | -255.911 | 0 |  | 10 | 15 | -103 | 7615.5 | 0 | 0 | 0 | 0 | 0 |  | 350 | -262.4159 | 0 | 175 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:36
2009-10-12 02:24 | 60.009 | 3667.3982 | 350 | -255.911 | 0 |  | 10 | 15 | -103 | 7615.83 | 0 | 0 | 0 | 0 | 0 |  | 350 | -262.4159 | 0 | 175.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:36
2009-10-12 02:24 | 60.009 | 3667.043 | 350 | -255.911 | 0 |  | 10 | 15 | -103 | 7616.16 | 0 | 0 | 0 | 0 | 0 |  | 350 | -262.4159 | 0 | 176 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:36
2009-10-12 02:24 | 60.005 | 3666.6235 | 350 | -255.911 | 0 |  | 10 | 15 | -103 | 7616.49 | 0 | 0 | 0 | -0.0039978 | 0.0039978 |  | 350 | -259.6852 | 0 | 176.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:36
2009-10-12 02:24 | 60.002 | 3666.2227 | 350 | -255.911 | 0 |  | 10 | 15 | -103 | 7616.82 | 0 | 0 | 0 | -0.0030022 | 0.0030022 |  | 350 | -259.6852 | 0 | 177 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:37
2009-10-12 02:24 | 59.999 | 3665.8796 | 350 | -258.1482 | 0 |  | 10 | 15 | -103 | 7617.15 | 0 | 0 | 0 | -0.0029984 | 0.0029984 |  | 350 | -259.6852 | 0 | 177.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:33 | 2009-10-12 02:37
2009-10-12 02:24 | 59.996 | 3665.4033 | 350 | -258.1482 | 0 |  | 10 | 15 | -103 | 7617.48 | 0 | 0 | 0 | -0.0030022 | 0.0030022 |  | 350 | -259.6852 | 0 | 178 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:37
2009-10-12 02:24 | 59.995 | 3665.8015 | 350 | -258.1482 | 0 |  | 10 | 15 | -103 | 7617.81 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -259.6852 | 0 | 178.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:37
2009-10-12 02:24 | 59.997 | 3665.6797 | 350 | -258.1482 | 0 |  | 10 | 15 | -103 | 7618.14 | 0 | 0 | 0 | 0.0020027 | 0.0020027 |  | 350 | -255.911 | 0 | 179 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:37
2009-10-12 02:24 | 59.998 | 3665.3521 | 350 | -258.1482 | 0 |  | 10 | 15 | -103 | 7618.47 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -255.911 | 0 | 179.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:34 | 2009-10-12 02:37
2009-10-12 02:24 | 59.998 | 3664.9475 | 350 | -258.8736 | 0 |  | 10 | 15 | -103 | 7618.8 | 0 | 0 | 0 | 0 | 0 |  | 350 | -255.911 | 0 | 180 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:34 | 2009-10-12 02:37
2009-10-12 02:24 | 59.998 | 3665.0649 | 350 | -258.8736 | 0 |  | 10 | 15 | -103 | 7619.13 | 0 | 0 | 0 | 0 | 0 |  | 350 | -255.911 | 0 | 180.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:34 | 2009-10-12 02:37
2009-10-12 02:24 | 59.998 | 3666.1333 | 350 | -258.8736 | 0 |  | 10 | 15 | -103 | 7619.46 | 0 | 0 | 0 | 0 | 0 |  | 350 | -255.911 | 0 | 181 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:34 | 2009-10-12 02:37
2009-10-12 02:24 | 59.995 | 3666.6396 | 350 | -258.8736 | 0 |  | 10 | 15 | -103 | 7619.79 | 0 | 0 | 0 | -0.0030022 | 0.0030022 |  | 350 | -258.1482 | 0 | 181.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:34 | 2009-10-12 02:37
2009-10-12 02:24 | 59.995 | 3666.7346 | 350 | -258.8736 | 0 |  | 10 | 15 | -103 | 7620.12 | 0 | 0 | 0 | 0 | 0 |  | 350 | -258.1482 | 0 | 182 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:34 | 2009-10-12 02:38
2009-10-12 02:24 | 59.992 | 3667.084 | 350 | -249.3376 | 0 |  | 10 | 15 | -103 | 7620.45 | 0 | 0 | 0 | -0.0029984 | 0.0029984 |  | 350 | -258.1482 | 0 | 182.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:34 | 2009-10-12 02:38
2009-10-12 02:24 | 59.993 | 3667.5574 | 350 | -249.3376 | 0 |  | 10 | 15 | -103 | 7620.78 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -258.1482 | 0 | 183 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:34 | 2009-10-12 02:38
2009-10-12 02:24 | 59.988 | 3667.3367 | 350 | -249.3376 | 0 |  | 10 | 15 | -103 | 7621.11 | 0 | 0 | 0 | -0.0050011 | 0.0050011 |  | 350 | -258.1482 | 0 | 183.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:34 | 2009-10-12 02:38
2009-10-12 02:24 | 59.988 | 3667.8533 | 350 | -249.3376 | 0 |  | 10 | 15 | -103 | 7621.44 | 0 | 0 | 0 | 0 | 0 |  | 350 | -258.8736 | 0 | 184 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:38
2009-10-12 02:24 | 59.982 | 3668.1165 | 350 | -249.3376 | 0 |  | 10 | 15 | -103 | 7621.77 | 0 | 0 | 0 | -0.0060005 | 0.0060005 |  | 350 | -258.8736 | 0 | 184.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:38
2009-10-12 02:24 | 59.982 | 3668.6909 | 350 | -258.2782 | 0 |  | 10 | 15 | -103 | 7622.1 | 0 | 0 | 0 | 0 | 0 |  | 350 | -258.8736 | 0 | 185 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:38
2009-10-12 02:24 | 59.982 | 3669.3992 | 350 | -258.2782 | 0 |  | 10 | 15 | -103 | 7622.43 | 0 | 0 | 0 | 0 | 0 |  | 350 | -258.8736 | 0 | 185.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:38
2009-10-12 02:24 | 59.982 | 3669.6062 | 350 | -258.2782 | 0 |  | 10 | 15 | -103 | 7622.76 | 0 | 0 | 0 | 0 | 0 |  | 350 | -258.8736 | 0 | 186 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:38
2009-10-12 02:24 | 59.984 | 3671.228 | 350 | -258.2782 | 0 |  | 10 | 15 | -103 | 7623.09 | 0 | 0 | 0 | 0.0020027 | 0.0020027 |  | 350 | -249.3376 | 0 | 186.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:28 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:38
2009-10-12 02:24 | 59.982 | 3670.25 | 350 | -258.2782 | 0 |  | 10 | 15 | -103 | 7623.42 | 0 | 0 | 0 | -0.0020027 | 0.0020027 |  | 350 | -249.3376 | 0 | 187 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:28 | 2009-10-12 02:32 | 2009-10-12 02:35 | 2009-10-12 02:39
2009-10-12 02:24 | 59.978 | 3670.2646 | 350 | -258.4064 | 0 |  | 10 | 15 | -103 | 7623.75 | 0 | 0 | 0 | -0.0039978 | 0.0039978 |  | 350 | -249.3376 | 0 | 187.5 | 10 | 15 | 2009-10-12 02:24 | 2009-10-12 02:28 | 2009-10-12 02:32 | 2009-10-12 02:35 | 2009-10-12 02:39
2009-10-12 02:25 | 59.978 | 3671.5488 | 350 | -258.4064 | 0 |  | 10 | 15 | -103 | 7624.08 | 0 | 0 | 0 | 0 | 0 |  | 350 | -249.3376 | 0 | 188 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:32 | 2009-10-12 02:35 | 2009-10-12 02:39
2009-10-12 02:25 | 59.976 | 3673.2432 | 350 | -258.4064 | 0 |  | 10 | 15 | -103 | 7624.41 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -249.3376 | 0 | 188.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:32 | 2009-10-12 02:35 | 2009-10-12 02:39
2009-10-12 02:25 | 59.975 | 3674.2629 | 350 | -258.4064 | 0 |  | 10 | 15 | -103 | 7624.74 | 0 | 0 | 0 | -0.0010033 | 0.0010033 |  | 350 | -258.2782 | 0 | 189 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:32 | 2009-10-12 02:35 | 2009-10-12 02:39
2009-10-12 02:25 | 59.974 | 3675.8245 | 350 | -258.4064 | 0 |  | 10 | 15 | -103 | 7625.07 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -258.2782 | 0 | 189.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:32 | 2009-10-12 02:35 | 2009-10-12 02:39
2009-10-12 02:25 | 59.974 | 3676.4182 | 350 | -260.5389 | 0 |  | 10 | 15 | -103 | 7625.4 | 0 | 0 | 0 | 0 | 0 |  | 350 | -258.2782 | 0 | 190 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:39
2009-10-12 02:25 | 59.979 | 3676.3057 | 350 | -260.5389 | 0 |  | 10 | 15 | -103 | 7625.73 | 0 | 0 | 0 | 0.0050011 | 0.0050011 |  | 350 | -258.2782 | 0 | 190.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:39
2009-10-12 02:25 | 59.98 | 3674.6375 | 350 | -260.5389 | 0 |  | 10 | 15 | -103 | 7626.06 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -258.2782 | 0 | 191 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:39
2009-10-12 02:25 | 59.981 | 3675.3289 | 350 | -260.5389 | 0 |  | 10 | 15 | -103 | 7626.39 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -258.4064 | 0 | 191.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:39
2009-10-12 02:25 | 59.98 | 3675.2261 | 350 | -260.5389 | 0 |  | 10 | 15 | -103 | 7626.72 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -258.4064 | 0 | 192 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:28 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:40
2009-10-12 02:25 | 59.984 | 3674.7681 | 350 | -257.8821 | 0 |  | 10 | 15 | -103 | 7627.05 | 0 | 0 | 0 | 0.0040016 | 0.0040016 |  | 350 | -258.4064 | 0 | 192.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:40
2009-10-12 02:25 | 59.987 | 3674.3994 | 350 | -257.8821 | 0 |  | 10 | 15 | -103 | 7627.38 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -258.4064 | 0 | 193 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:40
2009-10-12 02:25 | 59.988 | 3673.5142 | 350 | -257.8821 | 0 |  | 10 | 15 | -103 | 7627.71 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -258.4064 | 0 | 193.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:40
2009-10-12 02:25 | 59.988 | 3673.0396 | 350 | -257.8821 | 0 |  | 10 | 15 | -103 | 7628.04 | 0 | 0 | 0 | 0 | 0 |  | 350 | -260.5389 | 0 | 194 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:40
2009-10-12 02:25 | 59.99 | 3672.4417 | 350 | -257.8821 | 0 |  | 10 | 15 | -103 | 7628.37 | 0 | 0 | 0 | 0.0020027 | 0.0020027 |  | 350 | -260.5389 | 0 | 194.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:36 | 2009-10-12 02:40
2009-10-12 02:25 | 59.992 | 3673.0564 | 350 | -258.5887 | 0 |  | 10 | 15 | -103 | 7628.7 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -260.5389 | 0 | 195 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:36 | 2009-10-12 02:40
2009-10-12 02:25 | 59.991 | 3671.6802 | 350 | -258.5887 | 0 |  | 10 | 15 | -103 | 7629.03 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -260.5389 | 0 | 195.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:36 | 2009-10-12 02:40
2009-10-12 02:25 | 59.991 | 3671.4932 | 350 | -258.5887 | 0 |  | 10 | 15 | -103 | 7629.36 | 0 | 0 | 0 | 0 | 0 |  | 350 | -260.5389 | 0 | 196 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:40
2009-10-12 02:25 | 59.991 | 3669.53 | 350 | -258.5887 | 0 |  | 10 | 15 | -103 | 7629.69 | 0 | 0 | 0 | 0 | 0 |  | 350 | -257.8821 | 0 | 196.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:40
2009-10-12 02:25 | 59.993 | 3670.0662 | 350 | -258.5887 | 0 |  | 10 | 15 | -103 | 7630.02 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -257.8821 | 0 | 197 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:41
2009-10-12 02:25 | 59.993 | 3670.0278 | 350 | -261.9062 | 0 |  | 10 | 15 | -103 | 7630.35 | 0 | 0 | 0 | 0 | 0 |  | 350 | -257.8821 | 0 | 197.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:41
2009-10-12 02:25 | 59.996 | 3671.7441 | 350 | -261.9062 | 0 |  | 10 | 15 | -103 | 7630.68 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -257.8821 | 0 | 198 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:41
2009-10-12 02:25 | 60.002 | 3671.5781 | 350 | -261.9062 | 0 |  | 10 | 15 | -103 | 7631.01 | 0 | 0 | 0 | 0.0060005 | 0.0060005 |  | 350 | -257.8821 | 0 | 198.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:41
2009-10-12 02:25 | 60.002 | 3672.6255 | 350 | -261.9062 | 0 |  | 10 | 15 | -103 | 7631.34 | 0 | 0 | 0 | 0 | 0 |  | 350 | -258.5887 | 0 | 199 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:41
2009-10-12 02:25 | 60.003 | 3672.6741 | 350 | -261.9062 | 0 |  | 10 | 15 | -103 | 7631.67 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -258.5887 | 0 | 199.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:41
2009-10-12 02:25 | 60.004 | 3673.8186 | 350 | -256.7478 | 0 |  | 10 | 15 | -103 | 7632 | 0 | 0 | 0 | 0.0010033 | 0.0010033 |  | 350 | -258.5887 | 0 | 200 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:41
2009-10-12 02:25 | 60.005 | 3673.2495 | 350 | -256.7478 | 0 |  | 10 | 15 | -103 | 7632.33 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -258.5887 | 0 | 200.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:41
2009-10-12 02:25 | 60.004 | 3673.1821 | 350 | -256.7478 | 0 |  | 10 | 15 | -103 | 7632.66 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -258.5887 | 0 | 201 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:41
2009-10-12 02:25 | 60.002 | 3673.4963 | 350 | -256.7478 | 0 |  | 10 | 15 | -103 | 7632.99 | 0 | 0 | 0 | -0.0020027 | 0.0020027 |  | 350 | -261.9062 | 0 | 201.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:33 | 2009-10-12 02:37 | 2009-10-12 02:41
2009-10-12 02:25 | 60.004 | 3672.418 | 350 | -256.7478 | 0 |  | 10 | 15 | -103 | 7633.32 | 0 | 0 | 0 | 0.0020027 | 0.0020027 |  | 350 | -261.9062 | 0 | 202 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:29 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:42
2009-10-12 02:25 | 60.008 | 3672.363 | 350 | -167.432 | 0 |  | 10 | 15 | -103 | 7633.65 | 0 | 0 | 0 | 0.0039978 | 0.0039978 |  | 350 | -261.9062 | 0 | 202.5 | 10 | 15 | 2009-10-12 02:25 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:42
2009-10-12 02:26 | 60.01 | 3672.2168 | 350 | -167.432 | 0 |  | 10 | 15 | -103 | 7633.98 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -261.9062 | 0 | 203 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:42
2009-10-12 02:26 | 60.01 | 3672.2607 | 350 | -167.432 | 0 |  | 10 | 15 | -103 | 7634.31 | 0 | 0 | 0 | 0 | 0 |  | 350 | -261.9062 | 0 | 203.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:42
2009-10-12 02:26 | 60.01 | 3673.1821 | 350 | -167.432 | 0 |  | 10 | 15 | -103 | 7634.64 | 0 | 0 | 0 | 0 | 0 |  | 350 | -256.7478 | 0 | 204 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:42
2009-10-12 02:26 | 60.011 | 3673.6033 | 350 | -167.432 | 0 |  | 10 | 15 | -103 | 7634.97 | 0 | 0 | 0 | 0.0010033 | 0.0010033 |  | 350 | -256.7478 | 0 | 204.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:42
2009-10-12 02:26 | 60.013 | 3673.5535 | 350 | -164.9734 | 0 |  | 10 | 15 | -103 | 7635.3 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -256.7478 | 0 | 205 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:42
2009-10-12 02:26 | 60.014 | 3674.312 | 350 | -164.9734 | 0 |  | 10 | 15 | -103 | 7635.63 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -256.7478 | 0 | 205.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:42
2009-10-12 02:26 | 60.013 | 3674.5371 | 350 | -164.9734 | 0 |  | 10 | 15 | -103 | 7635.96 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -256.7478 | 0 | 206 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:42
2009-10-12 02:26 | 60.012 | 3673.8125 | 350 | -164.9734 | 0 |  | 10 | 15 | -103 | 7636.29 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -167.432 | 0 | 206.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:42
2009-10-12 02:26 | 60.011 | 3673.2036 | 350 | -164.9734 | 0 |  | 10 | 15 | -103 | 7636.62 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -167.432 | 0 | 207 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:43
2009-10-12 02:26 | 60.011 | 3672.5632 | 350 | -157.6281 | 0 |  | 10 | 15 | -103 | 7636.95 | 0 | 0 | 0 | 0 | 0 |  | 350 | -167.432 | 0 | 207.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:38 | 2009-10-12 02:43
2009-10-12 02:26 | 60.017 | 3673.0676 | 350 | -157.6281 | 0 |  | 10 | 15 | -103 | 7637.28 | 0 | 0 | 0 | 0.0059967 | 0.0059967 |  | 350 | -167.432 | 0 | 208 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:43
2009-10-12 02:26 | 60.022 | 3672.3882 | 350 | -157.6281 | 0 |  | 10 | 15 | -103 | 7637.61 | 0 | 0 | 0 | 0.0050011 | 0.0050011 |  | 350 | -167.432 | 0 | 208.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:43
2009-10-12 02:26 | 60.017 | 3672.5195 | 350 | -157.6281 | 0 |  | 10 | 15 | -103 | 7637.94 | 0 | 0 | 0 | -0.0050011 | 0.0050011 |  | 350 | -164.9734 | 0 | 209 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:43
2009-10-12 02:26 | 60.014 | 3671.25 | 350 | -157.6281 | 0 |  | 10 | 15 | -103 | 7638.27 | 0 | 0 | 0 | -0.0029984 | 0.0029984 |  | 350 | -164.9734 | 0 | 209.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:35 | 2009-10-12 02:39 | 2009-10-12 02:43
2009-10-12 02:26 | 60.013 | 3671.2881 | 350 | -155.5317 | 0 |  | 10 | 15 | -103 | 7638.6 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -164.9734 | 0 | 210 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:35 | 2009-10-12 02:39 | 2009-10-12 02:43
2009-10-12 02:26 | 60.014 | 3672.989 | 350 | -155.5317 | 0 |  | 10 | 15 | -103 | 7638.93 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -164.9734 | 0 | 210.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:35 | 2009-10-12 02:39 | 2009-10-12 02:43
2009-10-12 02:26 | 60.017 | 3672.9817 | 350 | -155.5317 | 0 |  | 10 | 15 | -103 | 7639.26 | 0 | 0 | 0 | 0.0029984 | 0.0029984 |  | 350 | -164.9734 | 0 | 211 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:35 | 2009-10-12 02:39 | 2009-10-12 02:43
2009-10-12 02:26 | 60.017 | 3672.9153 | 350 | -155.5317 | 0 |  | 10 | 15 | -103 | 7639.59 | 0 | 0 | 0 | 0 | 0 |  | 350 | -157.6281 | 0 | 211.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:35 | 2009-10-12 02:39 | 2009-10-12 02:43
2009-10-12 02:26 | 60.019 | 3671.9517 | 350 | -155.5317 | 0 |  | 10 | 15 | -103 | 7639.92 | 0 | 0 | 0 | 0.0020027 | 0.0020027 |  | 350 | -157.6281 | 0 | 212 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:30 | 2009-10-12 02:35 | 2009-10-12 02:39 | 2009-10-12 02:44
2009-10-12 02:26 | 60.019 | 3671.1931 | 350 | -160.4472 | 0 |  | 10 | 15 | -103 | 7640.25 | 0 | 0 | 0 | 0 | 0 |  | 350 | -157.6281 | 0 | 212.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:39 | 2009-10-12 02:44
2009-10-12 02:26 | 60.019 | 3671.6272 | 350 | -160.4472 | 0 |  | 10 | 15 | -103 | 7640.58 | 0 | 0 | 0 | 0 | 0 |  | 350 | -157.6281 | 0 | 213 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:39 | 2009-10-12 02:44
2009-10-12 02:26 | 60.027 | 3671.189 | 350 | -160.4472 | 0 |  | 10 | 15 | -103 | 7640.91 | 0 | 0 | 0 | 0.0079994 | 0.0079994 |  | 350 | -157.6281 | 0 | 213.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:39 | 2009-10-12 02:44
2009-10-12 02:26 | 60.026 | 3668.6106 | 350 | -160.4472 | 0 |  | 10 | 15 | -103 | 7641.24 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -155.5317 | 0 | 214 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:40 | 2009-10-12 02:44
2009-10-12 02:26 | 60.026 | 3665.2322 | 350 | -160.4472 | 0 |  | 10 | 15 | -103 | 7641.57 | 0 | 0 | 0 | 0 | 0 |  | 350 | -155.5317 | 0 | 214.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:40 | 2009-10-12 02:44
2009-10-12 02:26 | 60.022 | 3664.4951 | 350 | -163.9586 | 0 |  | 10 | 15 | -103 | 7641.9 | 0 | 0 | 0 | -0.0040016 | 0.0040016 |  | 350 | -155.5317 | 0 | 215 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:40 | 2009-10-12 02:44
2009-10-12 02:26 | 60.019 | 3666.0618 | 350 | -163.9586 | 0 |  | 10 | 15 | -103 | 7642.23 | 0 | 0 | 0 | -0.0029984 | 0.0029984 |  | 350 | -155.5317 | 0 | 215.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:40 | 2009-10-12 02:44
2009-10-12 02:26 | 60.017 | 3666.8208 | 350 | -163.9586 | 0 |  | 10 | 15 | -103 | 7642.56 | 0 | 0 | 0 | -0.0020027 | 0.0020027 |  | 350 | -155.5317 | 0 | 216 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:40 | 2009-10-12 02:44
2009-10-12 02:26 | 60.019 | 3666.7874 | 350 | -163.9586 | 0 |  | 10 | 15 | -103 | 7642.89 | 0 | 0 | 0 | 0.0020027 | 0.0020027 |  | 350 | -160.4472 | 0 | 216.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:31 | 2009-10-12 02:35 | 2009-10-12 02:40 | 2009-10-12 02:44
2009-10-12 02:26 | 60.02 | 3670.4536 | 350 | -163.9586 | 0 |  | 10 | 15 | -103 | 7643.22 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -160.4472 | 0 | 217 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:31 | 2009-10-12 02:36 | 2009-10-12 02:40 | 2009-10-12 02:45
2009-10-12 02:26 | 60.019 | 3670.2668 | 350 | -166.0724 | 0 |  | 10 | 15 | -103 | 7643.55 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -160.4472 | 0 | 217.5 | 10 | 15 | 2009-10-12 02:26 | 2009-10-12 02:31 | 2009-10-12 02:36 | 2009-10-12 02:40 | 2009-10-12 02:45
2009-10-12 02:27 | 60.021 | 3671.668 | 350 | -166.0724 | 0 |  | 10 | 15 | -103 | 7643.88 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -160.4472 | 0 | 218 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:36 | 2009-10-12 02:40 | 2009-10-12 02:45
2009-10-12 02:27 | 60.021 | 3672.4932 | 350 | -166.0724 | 0 |  | 10 | 15 | -103 | 7644.21 | 0 | 0 | 0 | 0 | 0 |  | 350 | -160.4472 | 0 | 218.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:36 | 2009-10-12 02:40 | 2009-10-12 02:45
2009-10-12 02:27 | 60.021 | 3672.6851 | 350 | -166.0724 | 0 |  | 10 | 15 | -103 | 7644.54 | 0 | 0 | 0 | 0 | 0 |  | 350 | -163.9586 | 0 | 219 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:36 | 2009-10-12 02:40 | 2009-10-12 02:45
2009-10-12 02:27 | 60.019 | 3672.8574 | 350 | -166.0724 | 0 |  | 10 | 15 | -103 | 7644.87 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -163.9586 | 0 | 219.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:36 | 2009-10-12 02:40 | 2009-10-12 02:45
2009-10-12 02:27 | 60.018 | 3672.1641 | 350 | -163.7666 | 0 |  | 10 | 15 | -103 | 7645.2 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -163.9586 | 0 | 220 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:36 | 2009-10-12 02:41 | 2009-10-12 02:45
2009-10-12 02:27 | 60.022 | 3671.4131 | 350 | -163.7666 | 0 |  | 10 | 15 | -103 | 7645.53 | 0 | 0 | 0 | 0.0039978 | 0.0039978 |  | 350 | -163.9586 | 0 | 220.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:36 | 2009-10-12 02:41 | 2009-10-12 02:45
2009-10-12 02:27 | 60.031 | 3669.9829 | 350 | -163.7666 | 0 |  | 10 | 15 | -103 | 7645.86 | 0 | 0 | 0 | 0.0089989 | 0.0089989 |  | 350 | -163.9586 | 0 | 221 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:36 | 2009-10-12 02:41 | 2009-10-12 02:45
2009-10-12 02:27 | 60.037 | 3666.4673 | 350 | -163.7666 | 0 |  | 10 | 15 | -103 | 7646.19 | 0 | 0 | 0 | 0.0060005 | 0.0060005 |  | 350 | -166.0724 | 0 | 221.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:36 | 2009-10-12 02:41 | 2009-10-12 02:45
2009-10-12 02:27 | 60.037 | 3663.7581 | 350 | -163.7666 | 0 |  | 10 | 15 | -103 | 7646.52 | 0 | 0 | 0 | 0 | 0 |  | 350 | -166.0724 | 0 | 222 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:31 | 2009-10-12 02:36 | 2009-10-12 02:41 | 2009-10-12 02:46
2009-10-12 02:27 | 60.036 | 3661.5991 | 350 | -165.1017 | 0 |  | 10 | 15 | -103 | 7646.85 | 0 | 0 | 0 | -0.00099945 | 0.00099945 |  | 350 | -166.0724 | 0 | 222.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:41 | 2009-10-12 02:46
2009-10-12 02:27 | 60.037 | 3660.6724 | 350 | -165.1017 | 0 |  | 10 | 15 | -103 | 7647.18 | 0 | 0 | 0 | 0.00099945 | 0.00099945 |  | 350 | -166.0724 | 0 | 223 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:41 | 2009-10-12 02:46
2009-10-12 02:27 | 60.046 | 3651.4917 | 350 | -165.1017 | 0 |  | 10 | 15 | -103 | 7647.51 | 0 | 0 | 0 | 0.0090027 | 0.0090027 |  | 350 | -166.0724 | 0 | 223.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:41 | 2009-10-12 02:46
2009-10-12 02:27 | 60.048 | 3649.1904 | 350 | -165.1017 | 0 |  | 10 | 15 | -103 | 7647.84 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -163.7666 | 0 | 224 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:36 | 2009-10-12 02:41 | 2009-10-12 02:46
2009-10-12 02:27 | 60.048 | 3650.0251 | 350 | -165.1017 | 0 |  | 10 | 15 | -103 | 7648.17 | 0 | 0 | 0 | 0 | 0 |  | 350 | -163.7666 | 0 | 224.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:41 | 2009-10-12 02:46
2009-10-12 02:27 | 60.043 | 3648.2463 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7648.5 | 0 | 0 | 0 | -0.0050011 | 0.0050011 |  | 350 | -163.7666 | 0 | 225 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:41 | 2009-10-12 02:46
2009-10-12 02:27 | 60.041 | 3649.512 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7648.83 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -163.7666 | 0 | 225.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:41 | 2009-10-12 02:46
2009-10-12 02:27 | 60.041 | 3654.2944 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7649.16 | 0 | 0 | 0 | 0 | 0 |  | 350 | -163.7666 | 0 | 226 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:46
2009-10-12 02:27 | 60.041 | 3655.0068 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7649.49 | 0 | 0 | 0 | 0 | 0 |  | 350 | -165.1017 | 0 | 226.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:46
2009-10-12 02:27 | 60.039 | 3651.8743 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7649.82 | 0 | 0 | 0 | -0.0019989 | 0.0019989 |  | 350 | -165.1017 | 0 | 227 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:47
2009-10-12 02:27 | 60.041 | 3651.0593 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.15 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -165.1017 | 0 | 227.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:47
2009-10-12 02:27 | 60.043 | 3649.187 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.48 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -165.1017 | 0 | 228 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:47
2009-10-12 02:27 | 60.045 | 3648.2363 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.81 | 0 | 0 | 0 | 0.0019989 | 0.0019989 |  | 350 | -165.1017 | 0 | 228.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:47
2009-10-12 02:27 | 60.046 | 3645.387 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7651.14 | 0 | 0 | 0 | 0.0010033 | 0.0010033 |  | 350 | -165.4764 | 0 | 229 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:47
2009-10-12 02:27 | 60.041 | 3644.6277 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7651.47 | 0 | 0 | 0 | -0.0050011 | 0.0050011 |  | 350 | -165.4764 | 0 | 229.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:47
2009-10-12 02:27 | 60.041 | 3645.4458 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7651.8 | 0 | 0 | 0 | 0 | 0 |  | 350 | -165.4764 | 0 | 230 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:47
2009-10-12 02:27 | 60.041 | 3640.6821 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7652.13 | 0 | 0 | 0 | 0 | 0 |  | 350 | -165.4764 | 0 | 230.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:47
2009-10-12 02:27 | 60.039 | 3641.1912 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7652.46 | 0 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -165.4764 | 0 | 231 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:47
2009-10-12 02:27 | 59.978 | 3659.4648 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7652.79 | 0 | 0 | 1 | -0.061001 | 0.061001 |  | 350 | -206.4591 | 0 | 231.5 | 10 | 15 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:37 | 2009-10-12 02:42 | 2009-10-12 02:47
2009-10-12 02:27 | 59.852 | 3696.3623 | 335 | -211.256 | 1 |  | 10 | 0 | -103 | 7616 | 1 | 0 | 1 | -0.126 | 0.126 |  | 350 | -206.4591 | 0 | 232 | 10 | 0 | 2009-10-12 02:27 | 2009-10-12 02:32 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:48
2009-10-12 02:27 | 59.836 | 3734.9043 | 335 | -214.3467 | 1 |  | 10 | 0 | -103 | 7626 | 1 | 0 | 1 | -0.016003 | 0.016003 |  | 335 | -206.4591 | 0 | 232.5 | 10 | 0 | 2009-10-12 02:27 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:48
2009-10-12 02:28 | 59.869 | 3734.6726 | 335 | -214.3467 | 1 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.033001 | 0.033001 |  | 335 | -206.4591 | 0 | 233 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:48
2009-10-12 02:28 | 59.892 | 3737.1567 | 335 | -214.3467 | 1 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.022999 | 0.022999 |  | 335 | -206.4591 | 0 | 233.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:48
2009-10-12 02:28 | 59.891 | 3761.2495 | 335 | -214.3467 | 2 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -211.256 | 0 | 234 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:48
2009-10-12 02:28 | 59.88 | 3766.113 | 335 | -214.3467 | 3 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.010998 | 0.010998 |  | 335 | -211.256 | 1 | 234.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:48
2009-10-12 02:28 | 59.876 | 3766.1938 | 335 | -212.1727 | 4 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 335 | -211.256 | 1 | 235 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:48
2009-10-12 02:28 | 59.875 | 3768.877 | 335 | -212.1727 | 5 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -211.256 | 1 | 235.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:48
2009-10-12 02:28 | 59.883 | 3769.925 | 335 | -212.1727 | 6 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.0079994 | 0.0079994 |  | 335 | -211.256 | 1 | 236 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:48
2009-10-12 02:28 | 59.887 | 3780.6206 | 335 | -212.1727 | 7 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 335 | -214.3467 | 1 | 236.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:48
2009-10-12 02:28 | 59.886 | 3781.5918 | 335 | -212.1727 | 8 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -214.3467 | 1 | 237 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:49
2009-10-12 02:28 | 59.885 | 3782.4995 | 335 | -215.5982 | 9 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 335 | -214.3467 | 1 | 237.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:43 | 2009-10-12 02:49
2009-10-12 02:28 | 59.887 | 3784.9619 | 335 | -215.5982 | 10 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 335 | -214.3467 | 2 | 238 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:44 | 2009-10-12 02:49
2009-10-12 02:28 | 59.888 | 3784.7297 | 335 | -215.5982 | 11 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 335 | -214.3467 | 3 | 238.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:44 | 2009-10-12 02:49
2009-10-12 02:28 | 59.89 | 3784.4189 | 335 | -215.5982 | 12 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 335 | -212.1727 | 4 | 239 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:38 | 2009-10-12 02:44 | 2009-10-12 02:49
2009-10-12 02:28 | 59.895 | 3788.0723 | 335 | -215.5982 | 13 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 335 | -212.1727 | 5 | 239.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:39 | 2009-10-12 02:44 | 2009-10-12 02:49
2009-10-12 02:28 | 59.894 | 3788.3276 | 335 | -218.3273 | 14 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -212.1727 | 6 | 240 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:39 | 2009-10-12 02:44 | 2009-10-12 02:49
2009-10-12 02:28 | 59.893 | 3788.8684 | 335 | -218.3273 | 15 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -212.1727 | 7 | 240.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:39 | 2009-10-12 02:44 | 2009-10-12 02:49
2009-10-12 02:28 | 59.894 | 3788.4719 | 335 | -218.3273 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 335 | -212.1727 | 8 | 241 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:39 | 2009-10-12 02:44 | 2009-10-12 02:49
2009-10-12 02:28 | 59.894 | 3792.2756 | 335 | -218.3273 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0 | 0 |  | 335 | -215.5982 | 9 | 241.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:39 | 2009-10-12 02:44 | 2009-10-12 02:49
2009-10-12 02:28 | 59.891 | 3793.0745 | 335 | -218.3273 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 335 | -215.5982 | 10 | 242 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:33 | 2009-10-12 02:39 | 2009-10-12 02:44 | 2009-10-12 02:50
2009-10-12 02:28 | 59.89 | 3794.3743 | 335 | -217.3794 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -215.5982 | 11 | 242.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:44 | 2009-10-12 02:50
2009-10-12 02:28 | 59.885 | 3799.4277 | 335 | -217.3794 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 335 | -215.5982 | 12 | 243 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:44 | 2009-10-12 02:50
2009-10-12 02:28 | 59.885 | 3800.4275 | 335 | -217.3794 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0 | 0 |  | 335 | -215.5982 | 13 | 243.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:44 | 2009-10-12 02:50
2009-10-12 02:28 | 59.888 | 3799.9592 | 335 | -217.3794 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 335 | -218.3273 | 14 | 244 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:45 | 2009-10-12 02:50
2009-10-12 02:28 | 59.887 | 3803.625 | 335 | -217.3794 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -218.3273 | 15 | 244.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:45 | 2009-10-12 02:50
2009-10-12 02:28 | 59.888 | 3802.925 | 335 | -214.8304 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 335 | -218.3273 | 16 | 245 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:45 | 2009-10-12 02:50
2009-10-12 02:28 | 59.888 | 3802.9509 | 335 | -214.8304 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0 | 0 |  | 335 | -218.3273 | 16 | 245.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:45 | 2009-10-12 02:50
2009-10-12 02:28 | 59.89 | 3804.3879 | 335 | -214.8304 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 335 | -218.3273 | 16 | 246 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:45 | 2009-10-12 02:50
2009-10-12 02:28 | 59.889 | 3805.4961 | 335 | -214.8304 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.00099939 | 0.00099939 |  | 335 | -217.3794 | 16 | 246.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:34 | 2009-10-12 02:39 | 2009-10-12 02:45 | 2009-10-12 02:50
2009-10-12 02:28 | 59.882 | 3805.6167 | 335 | -214.8304 | 16 |  | 10 | 0 | -103 | 7632 | 1 | 0 | 1 | -0.007 | 0.007 |  | 335 | -217.3794 | 16 | 247 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:34 | 2009-10-12 02:40 | 2009-10-12 02:45 | 2009-10-12 02:51
2009-10-12 02:28 | 59.873 | 3809.2373 | 335 | -227.6559 | 16 |  | 10 | 0 | -103 | 7631 | 1 | 0 | 1 | -0.0089989 | 0.0089989 |  | 335 | -217.3794 | 16 | 247.5 | 10 | 0 | 2009-10-12 02:28 | 2009-10-12 02:34 | 2009-10-12 02:40 | 2009-10-12 02:45 | 2009-10-12 02:51
2009-10-12 02:29 | 59.857 | 3811.5029 | 335 | -227.6559 | 16 |  | 10 | 0 | -103 | 7625 | 1 | 0 | 1 | -0.016003 | 0.016003 |  | 335 | -217.3794 | 16 | 248 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:34 | 2009-10-12 02:40 | 2009-10-12 02:45 | 2009-10-12 02:51
2009-10-12 02:29 | 59.849 | 3814.8623 | 335 | -227.6559 | 16 |  | 10 | 0 | -103 | 7623 | 1 | 0 | 1 | -0.0079994 | 0.0079994 |  | 335 | -217.3794 | 16 | 248.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:34 | 2009-10-12 02:40 | 2009-10-12 02:45 | 2009-10-12 02:51
2009-10-12 02:29 | 59.852 | 3815.8889 | 335 | -227.6559 | 16 |  | 10 | 0 | -103 | 7621 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 335 | -214.8304 | 16 | 249 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:34 | 2009-10-12 02:40 | 2009-10-12 02:45 | 2009-10-12 02:51
2009-10-12 02:29 | 59.858 | 3825.6426 | 335 | -227.6559 | 16 |  | 10 | 0 | -103 | 7623 | 1 | 0 | 1 | 0.0060005 | 0.0060005 |  | 335 | -214.8304 | 16 | 249.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:34 | 2009-10-12 02:40 | 2009-10-12 02:45 | 2009-10-12 02:51
2009-10-12 02:29 | 59.863 | 3826.0532 | 335 | -225.0181 | 16 |  | 10 | 0 | -103 | 7625 | 1 | 0 | 1 | 0.0049973 | 0.0049973 |  | 335 | -214.8304 | 16 | 250 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:34 | 2009-10-12 02:40 | 2009-10-12 02:46 | 2009-10-12 02:51
2009-10-12 02:29 | 59.866 | 3826.0024 | 335 | -225.0181 | 16 |  | 10 | 0 | -103 | 7627 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 335 | -214.8304 | 16 | 250.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:34 | 2009-10-12 02:40 | 2009-10-12 02:46 | 2009-10-12 02:51
2009-10-12 02:29 | 59.865 | 3827.5239 | 335 | -225.0181 | 16 |  | 10 | 0 | -103 | 7628 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -214.8304 | 16 | 251 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:34 | 2009-10-12 02:40 | 2009-10-12 02:46 | 2009-10-12 02:51
2009-10-12 02:29 | 59.867 | 3826.7532 | 335 | -225.0181 | 16 |  | 10 | 0 | -103 | 7628 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 335 | -227.6559 | 16 | 251.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:34 | 2009-10-12 02:40 | 2009-10-12 02:46 | 2009-10-12 02:51
2009-10-12 02:29 | 59.866 | 3826.7834 | 335 | -225.0181 | 16 |  | 10 | 0 | -103 | 7629 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -227.6559 | 16 | 252 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:34 | 2009-10-12 02:40 | 2009-10-12 02:46 | 2009-10-12 02:52
2009-10-12 02:29 | 59.871 | 3826.4536 | 335 | -228.3652 | 16 |  | 10 | 0 | -103 | 7630 | 1 | 0 | 1 | 0.0049973 | 0.0049973 |  | 335 | -227.6559 | 16 | 252.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:40 | 2009-10-12 02:46 | 2009-10-12 02:52
2009-10-12 02:29 | 59.874 | 3825.7134 | 335 | -228.3652 | 16 |  | 10 | 0 | -103 | 7631 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 335 | -227.6559 | 16 | 253 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:40 | 2009-10-12 02:46 | 2009-10-12 02:52
2009-10-12 02:29 | 59.879 | 3823.8257 | 335 | -228.3652 | 16 |  | 10 | 0 | -103 | 7635 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 335 | -227.6559 | 16 | 253.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:40 | 2009-10-12 02:46 | 2009-10-12 02:52
2009-10-12 02:29 | 59.88 | 3822.5054 | 335 | -228.3652 | 16 |  | 10 | 0 | -103 | 7638 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 335 | -225.0181 | 16 | 254 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:40 | 2009-10-12 02:46 | 2009-10-12 02:52
2009-10-12 02:29 | 59.883 | 3819.0811 | 335 | -228.3652 | 16 |  | 10 | 0 | -103 | 7639 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 335 | -225.0181 | 16 | 254.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:46 | 2009-10-12 02:52
2009-10-12 02:29 | 59.886 | 3818.0552 | 335 | -234.0753 | 16 |  | 10 | 0 | -103 | 7642 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 335 | -225.0181 | 16 | 255 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:46 | 2009-10-12 02:52
2009-10-12 02:29 | 59.89 | 3816.8147 | 335 | -234.0753 | 16 |  | 10 | 0 | -103 | 7644 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 335 | -225.0181 | 16 | 255.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:46 | 2009-10-12 02:52
2009-10-12 02:29 | 59.892 | 3815.0098 | 335 | -234.0753 | 16 |  | 10 | 0 | -103 | 7645 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 335 | -225.0181 | 16 | 256 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:52
2009-10-12 02:29 | 59.889 | 3813.7827 | 335 | -234.0753 | 16 |  | 10 | 0 | -103 | 7647 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 335 | -228.3652 | 16 | 256.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:52
2009-10-12 02:29 | 59.893 | 3811.8384 | 335 | -234.0753 | 16 |  | 10 | 0 | -103 | 7648 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 335 | -228.3652 | 16 | 257 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:53
2009-10-12 02:29 | 59.899 | 3809.6519 | 335 | -228.7982 | 16 |  | 10 | 0 | -103 | 7649 | 1 | 0 | 1 | 0.0059967 | 0.0059967 |  | 335 | -228.3652 | 16 | 257.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:53
2009-10-12 02:29 | 59.903 | 3806.9722 | 335 | -228.7982 | 16 |  | 10 | 0 | -103 | 7650 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 335 | -228.3652 | 16 | 258 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:53
2009-10-12 02:29 | 59.902 | 3805.5933 | 335 | -228.7982 | 16 |  | 10 | 0 | -103 | 7651 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -228.3652 | 16 | 258.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:53
2009-10-12 02:29 | 59.902 | 3804.1885 | 335 | -228.7982 | 16 |  | 10 | 0 | -103 | 7652 | 1 | 0 | 1 | 0 | 0 |  | 335 | -234.0753 | 16 | 259 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:53
2009-10-12 02:29 | 59.904 | 3796.0776 | 335 | -228.7982 | 16 |  | 10 | 0 | -103 | 7653 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 335 | -234.0753 | 16 | 259.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:53
2009-10-12 02:29 | 59.907 | 3793.9751 | 335 | -229.467 | 16 |  | 10 | 0 | -103 | 7654 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 335 | -234.0753 | 16 | 260 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:53
2009-10-12 02:29 | 59.911 | 3792.1694 | 335 | -229.467 | 16 |  | 10 | 0 | -103 | 7655 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 335 | -234.0753 | 16 | 260.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:53
2009-10-12 02:29 | 59.916 | 3791.502 | 335 | -229.467 | 16 |  | 10 | 0 | -103 | 7655 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 335 | -234.0753 | 16 | 261 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:53
2009-10-12 02:29 | 59.916 | 3789.5337 | 335 | -229.467 | 16 |  | 10 | 0 | -103 | 7656 | 1 | 0 | 1 | 0 | 0 |  | 335 | -228.7982 | 16 | 261.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:41 | 2009-10-12 02:47 | 2009-10-12 02:53
2009-10-12 02:29 | 59.917 | 3788.1321 | 335 | -229.467 | 16 |  | 10 | 0 | -103 | 7656 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 335 | -228.7982 | 16 | 262 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:35 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:54
2009-10-12 02:29 | 59.918 | 3784.5635 | 335 | -228.9802 | 16 |  | 10 | 0 | -103 | 7657 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 335 | -228.7982 | 16 | 262.5 | 10 | 0 | 2009-10-12 02:29 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:54
2009-10-12 02:30 | 59.92 | 3783.0283 | 335 | -228.9802 | 16 |  | 10 | 0 | -103 | 7657 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 335 | -228.7982 | 16 | 263 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:54
2009-10-12 02:30 | 59.921 | 3781.7012 | 335 | -228.9802 | 16 |  | 10 | 0 | -103 | 7658 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 335 | -228.7982 | 16 | 263.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:54
2009-10-12 02:30 | 59.92 | 3776.3584 | 335 | -228.9802 | 16 |  | 10 | 0 | -103 | 7658 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 335 | -229.467 | 16 | 264 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:54
2009-10-12 02:30 | 59.917 | 3775.6355 | 335 | -228.9802 | 16 |  | 10 | 0 | -103 | 7659 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 335 | -229.467 | 16 | 264.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:54
2009-10-12 02:30 | 59.92 | 3774.6042 | 335 | -219.9756 | 16 |  | 10 | 0 | -103 | 7659 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 335 | -229.467 | 16 | 265 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:54
2009-10-12 02:30 | 59.921 | 3773.3337 | 335 | -219.9756 | 16 |  | 10 | 0 | -103 | 7659 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 335 | -229.467 | 16 | 265.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:54
2009-10-12 02:30 | 59.923 | 3773.9578 | 335 | -219.9756 | 16 |  | 10 | 0 | -103 | 7660 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 335 | -229.467 | 16 | 266 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:54
2009-10-12 02:30 | 59.926 | 3772.7224 | 335 | -219.9756 | 16 |  | 10 | 0 | -103 | 7660 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 335 | -228.9802 | 16 | 266.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:54
2009-10-12 02:30 | 59.925 | 3771.6704 | 335 | -219.9756 | 16 |  | 10 | 0 | -103 | 7661 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -228.9802 | 16 | 267 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:55
2009-10-12 02:30 | 59.928 | 3769.6296 | 335 | -229.0892 | 16 |  | 10 | 0 | -103 | 7661 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 335 | -228.9802 | 16 | 267.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:48 | 2009-10-12 02:55
2009-10-12 02:30 | 59.927 | 3768.707 | 335 | -229.0892 | 16 |  | 10 | 0 | -103 | 7662 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 335 | -228.9802 | 16 | 268 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:49 | 2009-10-12 02:55
2009-10-12 02:30 | 59.932 | 3767.6428 | 335 | -229.0892 | 16 |  | 10 | 0 | -103 | 7662 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 335 | -228.9802 | 16 | 268.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:49 | 2009-10-12 02:55
2009-10-12 02:30 | 59.927 | 3767.021 | 335 | -229.0892 | 16 |  | 10 | 0 | -103 | 7663 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 335 | -219.9756 | 16 | 269 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:42 | 2009-10-12 02:49 | 2009-10-12 02:55
2009-10-12 02:30 | 59.928 | 3767.408 | 335 | -229.0892 | 16 |  | 10 | 0 | -103 | 7663 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 335 | -219.9756 | 16 | 269.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:43 | 2009-10-12 02:49 | 2009-10-12 02:55
2009-10-12 02:30 | 59.931 | 3766.7881 | 335 | -229.6633 | 16 |  | 10 | 0 | -103 | 7664 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 335 | -219.9756 | 16 | 270 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:43 | 2009-10-12 02:49 | 2009-10-12 02:55
2009-10-12 02:30 | 59.929 | 3766.259 | 335 | -229.6633 | 16 |  | 10 | 0 | -103 | 7664 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 335 | -219.9756 | 16 | 270.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:43 | 2009-10-12 02:49 | 2009-10-12 02:55
2009-10-12 02:30 | 59.931 | 3765.6716 | 335 | -229.6633 | 16 |  | 10 | 0 | -103 | 7665 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 335 | -219.9756 | 16 | 271 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:43 | 2009-10-12 02:49 | 2009-10-12 02:55
2009-10-12 02:30 | 59.933 | 3766.1226 | 335 | -229.6633 | 16 |  | 10 | 0 | -103 | 7666 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 335 | -229.0892 | 16 | 271.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:43 | 2009-10-12 02:49 | 2009-10-12 02:55
2009-10-12 02:30 | 59.937 | 3764.2427 | 335 | -229.6633 | 16 |  | 10 | 0 | -103 | 7666 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 335 | -229.0892 | 16 | 272 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:36 | 2009-10-12 02:43 | 2009-10-12 02:49 | 2009-10-12 02:56
2009-10-12 02:30 | 59.937 | 3765.105 | 335 | -229.2339 | 16 |  | 10 | 0 | -103 | 7667 | 1 | 0 | 1 | 0 | 0 |  | 335 | -229.0892 | 16 | 272.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:37 | 2009-10-12 02:43 | 2009-10-12 02:49 | 2009-10-12 02:56
2009-10-12 02:30 | 59.945 | 3762.9353 | 335 | -229.2339 | 16 |  | 10 | 0 | -103 | 7668 | 1 | 0 | 1 | 0.0079994 | 0.0079994 |  | 335 | -229.0892 | 16 | 273 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:37 | 2009-10-12 02:43 | 2009-10-12 02:49 | 2009-10-12 02:56
2009-10-12 02:30 | 59.949 | 3758.3872 | 335 | -229.2339 | 16 |  | 10 | 0 | -103 | 7668 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 335 | -229.0892 | 16 | 273.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:37 | 2009-10-12 02:43 | 2009-10-12 02:49 | 2009-10-12 02:56
2009-10-12 02:30 | 59.947 | 3753.9224 | 335 | -229.2339 | 16 |  | 10 | 0 | -103 | 7669 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 335 | -229.6633 | 16 | 274 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:37 | 2009-10-12 02:43 | 2009-10-12 02:50 | 2009-10-12 02:56
2009-10-12 02:30 | 59.942 | 3749.8672 | 350 | -229.2339 | 16 |  | 10 | 0 | -103 | 7669 | 1 | 0 | 1 | -0.0049973 | 0.0049973 |  | 335 | -229.6633 | 16 | 274.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:37 | 2009-10-12 02:43 | 2009-10-12 02:50 | 2009-10-12 02:56
2009-10-12 02:30 | 59.941 | 3746.8887 | 350 | -231.4099 | 16 |  | 10 | 0 | -103 | 7670 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 335 | -229.6633 | 16 | 275 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:37 | 2009-10-12 02:43 | 2009-10-12 02:50 | 2009-10-12 02:56
2009-10-12 02:30 | 59.942 | 3747.8755 | 350 | -231.4099 | 16 |  | 10 | 0 | -103 | 7670 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 335 | -229.6633 | 16 | 275.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:37 | 2009-10-12 02:43 | 2009-10-12 02:50 | 2009-10-12 02:56
2009-10-12 02:30 | 59.945 | 3749.5933 | 350 | -231.4099 | 16 |  | 10 | 0 | -103 | 7671 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 335 | -229.6633 | 16 | 276 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:37 | 2009-10-12 02:43 | 2009-10-12 02:50 | 2009-10-12 02:56
2009-10-12 02:30 | 59.948 | 3748.6611 | 350 | -231.4099 | 16 |  | 10 | 0 | -103 | 7671 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 335 | -229.2339 | 16 | 276.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:37 | 2009-10-12 02:43 | 2009-10-12 02:50 | 2009-10-12 02:56
2009-10-12 02:30 | 59.947 | 3746.7061 | 350 | -231.4099 | 16 |  | 10 | 0 | -103 | 7672 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 335 | -229.2339 | 16 | 277 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:37 | 2009-10-12 02:44 | 2009-10-12 02:50 | 2009-10-12 02:57
2009-10-12 02:30 | 59.949 | 3749.0769 | 350 | -218.6223 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 335 | -229.2339 | 16 | 277.5 | 10 | 0 | 2009-10-12 02:30 | 2009-10-12 02:37 | 2009-10-12 02:44 | 2009-10-12 02:50 | 2009-10-12 02:57
2009-10-12 02:31 | 59.951 | 3742.7415 | 350 | -218.6223 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 335 | -229.2339 | 16 | 278 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:37 | 2009-10-12 02:44 | 2009-10-12 02:50 | 2009-10-12 02:57
2009-10-12 02:31 | 59.952 | 3740.259 | 350 | -218.6223 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -229.2339 | 16 | 278.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:37 | 2009-10-12 02:44 | 2009-10-12 02:50 | 2009-10-12 02:57
2009-10-12 02:31 | 59.953 | 3736.1392 | 350 | -218.6223 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -231.4099 | 16 | 279 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:37 | 2009-10-12 02:44 | 2009-10-12 02:50 | 2009-10-12 02:57
2009-10-12 02:31 | 59.951 | 3731.3821 | 350 | -218.6223 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -231.4099 | 16 | 279.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:37 | 2009-10-12 02:44 | 2009-10-12 02:50 | 2009-10-12 02:57
2009-10-12 02:31 | 59.952 | 3727.8384 | 350 | -213.5359 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -231.4099 | 16 | 280 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:37 | 2009-10-12 02:44 | 2009-10-12 02:51 | 2009-10-12 02:57
2009-10-12 02:31 | 59.952 | 3725.9517 | 350 | -213.5359 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0 | 0 |  | 350 | -231.4099 | 16 | 280.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:37 | 2009-10-12 02:44 | 2009-10-12 02:51 | 2009-10-12 02:57
2009-10-12 02:31 | 59.952 | 3722.6489 | 350 | -213.5359 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0 | 0 |  | 350 | -231.4099 | 16 | 281 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:37 | 2009-10-12 02:44 | 2009-10-12 02:51 | 2009-10-12 02:57
2009-10-12 02:31 | 59.955 | 3720.5781 | 350 | -213.5359 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -218.6223 | 16 | 281.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:37 | 2009-10-12 02:44 | 2009-10-12 02:51 | 2009-10-12 02:57
2009-10-12 02:31 | 59.952 | 3717.9961 | 350 | -213.5359 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -218.6223 | 16 | 282 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:37 | 2009-10-12 02:44 | 2009-10-12 02:51 | 2009-10-12 02:58
2009-10-12 02:31 | 59.954 | 3718.1418 | 350 | -225.6519 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -218.6223 | 16 | 282.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:44 | 2009-10-12 02:51 | 2009-10-12 02:58
2009-10-12 02:31 | 59.952 | 3715.7527 | 350 | -225.6519 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -218.6223 | 16 | 283 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:44 | 2009-10-12 02:51 | 2009-10-12 02:58
2009-10-12 02:31 | 59.953 | 3713.6938 | 350 | -225.6519 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -218.6223 | 16 | 283.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:44 | 2009-10-12 02:51 | 2009-10-12 02:58
2009-10-12 02:31 | 59.953 | 3713.4836 | 350 | -225.6519 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0 | 0 |  | 350 | -213.5359 | 16 | 284 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:44 | 2009-10-12 02:51 | 2009-10-12 02:58
2009-10-12 02:31 | 59.952 | 3710.8481 | 350 | -225.6519 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -213.5359 | 16 | 284.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:51 | 2009-10-12 02:58
2009-10-12 02:31 | 59.954 | 3710.8101 | 350 | -212.5736 | 16 |  | 10 | 0 | -103 | 7673 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -213.5359 | 16 | 285 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:51 | 2009-10-12 02:58
2009-10-12 02:31 | 59.954 | 3712.0918 | 350 | -212.5736 | 16 |  | 10 | 0 | -103 | 7674 | 1 | 0 | 1 | 0 | 0 |  | 350 | -213.5359 | 16 | 285.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:51 | 2009-10-12 02:58
2009-10-12 02:31 | 59.959 | 3714.6226 | 350 | -212.5736 | 16 |  | 10 | 0 | -103 | 7675 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -213.5359 | 16 | 286 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:58
2009-10-12 02:31 | 59.957 | 3715.1296 | 350 | -212.5736 | 16 |  | 10 | 0 | -103 | 7676 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -225.6519 | 16 | 286.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:58
2009-10-12 02:31 | 59.956 | 3716.1682 | 350 | -212.5736 | 16 |  | 10 | 0 | -103 | 7677 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -225.6519 | 16 | 287 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:59
2009-10-12 02:31 | 59.954 | 3716.4614 | 350 | -219.8973 | 16 |  | 10 | 0 | -103 | 7678 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -225.6519 | 16 | 287.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:59
2009-10-12 02:31 | 59.956 | 3716.98 | 350 | -219.8973 | 16 |  | 10 | 0 | -103 | 7679 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -225.6519 | 16 | 288 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:59
2009-10-12 02:31 | 59.955 | 3717.759 | 350 | -219.8973 | 16 |  | 10 | 0 | -103 | 7680 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -225.6519 | 16 | 288.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:59
2009-10-12 02:31 | 59.958 | 3722.3613 | 350 | -219.8973 | 16 |  | 10 | 0 | -103 | 7681 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -212.5736 | 16 | 289 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:59
2009-10-12 02:31 | 59.961 | 3721.9731 | 350 | -219.8973 | 16 |  | 10 | 0 | -103 | 7682 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -212.5736 | 16 | 289.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:59
2009-10-12 02:31 | 59.962 | 3722.658 | 350 | -231.1754 | 16 |  | 10 | 0 | -103 | 7684 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -212.5736 | 16 | 290 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:59
2009-10-12 02:31 | 59.962 | 3722.2666 | 350 | -231.1754 | 16 |  | 10 | 0 | -103 | 7685 | 1 | 0 | 1 | 0 | 0 |  | 350 | -212.5736 | 16 | 290.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:59
2009-10-12 02:31 | 59.968 | 3722.2776 | 350 | -231.1754 | 16 |  | 10 | 0 | -103 | 7687 | 1 | 0 | 1 | 0.0059967 | 0.0059967 |  | 350 | -212.5736 | 16 | 291 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:59
2009-10-12 02:31 | 59.966 | 3721.7866 | 350 | -231.1754 | 16 |  | 10 | 0 | -103 | 7689 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -219.8973 | 16 | 291.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:45 | 2009-10-12 02:52 | 2009-10-12 02:59
2009-10-12 02:31 | 59.966 | 3723.0908 | 350 | -231.1754 | 16 |  | 10 | 0 | -103 | 7690 | 1 | 0 | 1 | 0 | 0 |  | 350 | -219.8973 | 16 | 292 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:38 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:00
2009-10-12 02:31 | 59.968 | 3723.9839 | 350 | -226.6341 | 16 |  | 10 | 0 | -103 | 7692 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -219.8973 | 16 | 292.5 | 10 | 0 | 2009-10-12 02:31 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:00
2009-10-12 02:32 | 59.97 | 3723.4346 | 350 | -226.6341 | 16 |  | 10 | 0 | -103 | 7692 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -219.8973 | 16 | 293 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:00
2009-10-12 02:32 | 59.974 | 3723.8931 | 350 | -226.6341 | 16 |  | 10 | 0 | -103 | 7693 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 350 | -219.8973 | 16 | 293.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:00
2009-10-12 02:32 | 59.97 | 3725.4028 | 350 | -226.6341 | 16 |  | 10 | 0 | -103 | 7693 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -231.1754 | 16 | 294 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:00
2009-10-12 02:32 | 59.969 | 3727.1211 | 350 | -226.6341 | 16 |  | 10 | 0 | -103 | 7694 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -231.1754 | 16 | 294.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:00
2009-10-12 02:32 | 59.969 | 3728.053 | 350 | -227.2551 | 16 |  | 10 | 0 | -103 | 7694 | 1 | 0 | 1 | 0 | 0 |  | 350 | -231.1754 | 16 | 295 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:00
2009-10-12 02:32 | 59.97 | 3731.1299 | 350 | -227.2551 | 16 |  | 10 | 0 | -103 | 7695 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -231.1754 | 16 | 295.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:00
2009-10-12 02:32 | 59.971 | 3732.53 | 350 | -227.2551 | 16 |  | 10 | 0 | -103 | 7695 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -231.1754 | 16 | 296 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:00
2009-10-12 02:32 | 59.973 | 3733.3271 | 350 | -227.2551 | 16 |  | 10 | 0 | -103 | 7695 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -226.6341 | 16 | 296.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:00
2009-10-12 02:32 | 59.973 | 3736.5352 | 350 | -227.2551 | 16 |  | 10 | 0 | -103 | 7696 | 1 | 0 | 1 | 0 | 0 |  | 350 | -226.6341 | 16 | 297 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:01
2009-10-12 02:32 | 59.976 | 3736.9075 | 350 | -229.2902 | 16 |  | 10 | 0 | -103 | 7696 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -226.6341 | 16 | 297.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:53 | 2009-10-12 03:01
2009-10-12 02:32 | 59.978 | 3736.8218 | 350 | -229.2902 | 16 |  | 10 | 0 | -103 | 7697 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -226.6341 | 16 | 298 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:54 | 2009-10-12 03:01
2009-10-12 02:32 | 59.978 | 3738.6992 | 350 | -229.2902 | 16 |  | 10 | 0 | -103 | 7697 | 1 | 0 | 1 | 0 | 0 |  | 350 | -226.6341 | 16 | 298.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:54 | 2009-10-12 03:01
2009-10-12 02:32 | 59.976 | 3739.9438 | 350 | -229.2902 | 16 |  | 10 | 0 | -103 | 7697 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -227.2551 | 16 | 299 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:46 | 2009-10-12 02:54 | 2009-10-12 03:01
2009-10-12 02:32 | 59.978 | 3740.877 | 350 | -229.2902 | 16 |  | 10 | 0 | -103 | 7698 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -227.2551 | 16 | 299.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:47 | 2009-10-12 02:54 | 2009-10-12 03:01
2009-10-12 02:32 | 59.976 | 3741.7937 | 350 | -221.4614 | 16 |  | 10 | 0 | -103 | 7698 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -227.2551 | 16 | 300 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:47 | 2009-10-12 02:54 | 2009-10-12 03:01
2009-10-12 02:32 | 59.978 | 3745.2336 | 350 | -221.4614 | 16 |  | 10 | 0 | -103 | 7698.33 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -227.2551 | 16 | 300.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:47 | 2009-10-12 02:54 | 2009-10-12 03:01
2009-10-12 02:32 | 59.977 | 3746.6079 | 350 | -221.4614 | 16 |  | 10 | 0 | -103 | 7698.66 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -227.2551 | 16 | 301 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:47 | 2009-10-12 02:54 | 2009-10-12 03:01
2009-10-12 02:32 | 59.98 | 3748.2998 | 350 | -221.4614 | 16 |  | 10 | 0 | -103 | 7698.99 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -229.2902 | 16 | 301.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:47 | 2009-10-12 02:54 | 2009-10-12 03:01
2009-10-12 02:32 | 59.982 | 3750.7163 | 350 | -221.4614 | 16 |  | 10 | 0 | -103 | 7699.32 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -229.2902 | 16 | 302 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:39 | 2009-10-12 02:47 | 2009-10-12 02:54 | 2009-10-12 03:02
2009-10-12 02:32 | 59.981 | 3751.5576 | 350 | -241.2744 | 16 |  | 10 | 0 | -103 | 7699.65 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -229.2902 | 16 | 302.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:40 | 2009-10-12 02:47 | 2009-10-12 02:54 | 2009-10-12 03:02
2009-10-12 02:32 | 59.98 | 3752.7476 | 350 | -241.2744 | 16 |  | 10 | 0 | -103 | 7699.98 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -229.2902 | 16 | 303 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:40 | 2009-10-12 02:47 | 2009-10-12 02:54 | 2009-10-12 03:02
2009-10-12 02:32 | 59.979 | 3755.5986 | 350 | -241.2744 | 16 |  | 10 | 0 | -103 | 7700.31 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -229.2902 | 16 | 303.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:40 | 2009-10-12 02:47 | 2009-10-12 02:54 | 2009-10-12 03:02
2009-10-12 02:32 | 59.98 | 3756.4072 | 350 | -241.2744 | 16 |  | 10 | 0 | -103 | 7700.64 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -221.4614 | 16 | 304 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:40 | 2009-10-12 02:47 | 2009-10-12 02:55 | 2009-10-12 03:02
2009-10-12 02:32 | 59.979 | 3756.9753 | 350 | -241.2744 | 16 |  | 10 | 0 | -103 | 7700.97 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -221.4614 | 16 | 304.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:40 | 2009-10-12 02:47 | 2009-10-12 02:55 | 2009-10-12 03:02
2009-10-12 02:32 | 59.983 | 3760.4053 | 350 | -243.0719 | 16 |  | 10 | 0 | -103 | 7701.3 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -221.4614 | 16 | 305 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:40 | 2009-10-12 02:47 | 2009-10-12 02:55 | 2009-10-12 03:02
2009-10-12 02:32 | 59.983 | 3760.9822 | 350 | -243.0719 | 16 |  | 10 | 0 | -103 | 7701.63 | 1 | 0 | 1 | 0 | 0 |  | 350 | -221.4614 | 16 | 305.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:40 | 2009-10-12 02:47 | 2009-10-12 02:55 | 2009-10-12 03:02
2009-10-12 02:32 | 59.984 | 3761.407 | 350 | -243.0719 | 16 |  | 10 | 0 | -103 | 7701.96 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -221.4614 | 16 | 306 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:40 | 2009-10-12 02:47 | 2009-10-12 02:55 | 2009-10-12 03:02
2009-10-12 02:32 | 59.988 | 3762.7373 | 350 | -243.0719 | 16 |  | 10 | 0 | -103 | 7702.29 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 350 | -241.2744 | 16 | 306.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:40 | 2009-10-12 02:47 | 2009-10-12 02:55 | 2009-10-12 03:02
2009-10-12 02:32 | 59.989 | 3763.2122 | 350 | -243.0719 | 16 |  | 10 | 0 | -103 | 7702.62 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -241.2744 | 16 | 307 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:40 | 2009-10-12 02:48 | 2009-10-12 02:55 | 2009-10-12 03:03
2009-10-12 02:32 | 59.987 | 3764.9575 | 350 | -241.6702 | 16 |  | 10 | 0 | -103 | 7702.95 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -241.2744 | 16 | 307.5 | 10 | 0 | 2009-10-12 02:32 | 2009-10-12 02:40 | 2009-10-12 02:48 | 2009-10-12 02:55 | 2009-10-12 03:03
2009-10-12 02:33 | 59.987 | 3766.0852 | 350 | -241.6702 | 16 |  | 10 | 0 | -103 | 7703.28 | 1 | 0 | 1 | 0 | 0 |  | 350 | -241.2744 | 16 | 308 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:40 | 2009-10-12 02:48 | 2009-10-12 02:55 | 2009-10-12 03:03
2009-10-12 02:33 | 59.991 | 3766.4331 | 350 | -241.6702 | 16 |  | 10 | 0 | -103 | 7703.61 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -241.2744 | 16 | 308.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:40 | 2009-10-12 02:48 | 2009-10-12 02:55 | 2009-10-12 03:03
2009-10-12 02:33 | 59.993 | 3767.251 | 350 | -241.6702 | 16 |  | 10 | 0 | -103 | 7703.94 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -243.0719 | 16 | 309 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:40 | 2009-10-12 02:48 | 2009-10-12 02:55 | 2009-10-12 03:03
2009-10-12 02:33 | 59.992 | 3767.7925 | 350 | -241.6702 | 16 |  | 10 | 0 | -103 | 7704.27 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -243.0719 | 16 | 309.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:40 | 2009-10-12 02:48 | 2009-10-12 02:55 | 2009-10-12 03:03
2009-10-12 02:33 | 59.991 | 3768.6335 | 350 | -228.1493 | 16 |  | 10 | 0 | -103 | 7704.6 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -243.0719 | 16 | 310 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:40 | 2009-10-12 02:48 | 2009-10-12 02:56 | 2009-10-12 03:03
2009-10-12 02:33 | 59.989 | 3771.1465 | 350 | -228.1493 | 16 |  | 10 | 0 | -103 | 7704.93 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -243.0719 | 16 | 310.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:40 | 2009-10-12 02:48 | 2009-10-12 02:56 | 2009-10-12 03:03
2009-10-12 02:33 | 59.986 | 3772.4446 | 350 | -228.1493 | 16 |  | 10 | 0 | -103 | 7705.26 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -243.0719 | 16 | 311 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:40 | 2009-10-12 02:48 | 2009-10-12 02:56 | 2009-10-12 03:03
2009-10-12 02:33 | 59.983 | 3773.6948 | 350 | -228.1493 | 16 |  | 10 | 0 | -103 | 7705.59 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -241.6702 | 16 | 311.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:40 | 2009-10-12 02:48 | 2009-10-12 02:56 | 2009-10-12 03:03
2009-10-12 02:33 | 59.983 | 3774.6685 | 350 | -228.1493 | 16 |  | 10 | 0 | -103 | 7705.92 | 1 | 0 | 1 | 0 | 0 |  | 350 | -241.6702 | 16 | 312 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:40 | 2009-10-12 02:48 | 2009-10-12 02:56 | 2009-10-12 03:04
2009-10-12 02:33 | 59.988 | 3775.8408 | 350 | -235.129 | 16 |  | 10 | 0 | -103 | 7706.25 | 1 | 0 | 1 | 0.0049973 | 0.0049973 |  | 350 | -241.6702 | 16 | 312.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:48 | 2009-10-12 02:56 | 2009-10-12 03:04
2009-10-12 02:33 | 59.993 | 3775.3633 | 350 | -235.129 | 16 |  | 10 | 0 | -103 | 7706.58 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -241.6702 | 16 | 313 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:48 | 2009-10-12 02:56 | 2009-10-12 03:04
2009-10-12 02:33 | 59.996 | 3774.8662 | 350 | -235.129 | 16 |  | 10 | 0 | -103 | 7706.91 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -241.6702 | 16 | 313.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:48 | 2009-10-12 02:56 | 2009-10-12 03:04
2009-10-12 02:33 | 59.998 | 3775.4917 | 350 | -235.129 | 16 |  | 10 | 0 | -103 | 7707.24 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -228.1493 | 16 | 314 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:48 | 2009-10-12 02:56 | 2009-10-12 03:04
2009-10-12 02:33 | 59.999 | 3776.4202 | 350 | -235.129 | 16 |  | 10 | 0 | -103 | 7707.57 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -228.1493 | 16 | 314.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:56 | 2009-10-12 03:04
2009-10-12 02:33 | 60.001 | 3778.5537 | 350 | -246.4331 | 16 |  | 10 | 0 | -103 | 7707.9 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -228.1493 | 16 | 315 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:56 | 2009-10-12 03:04
2009-10-12 02:33 | 59.999 | 3779.6919 | 350 | -246.4331 | 16 |  | 10 | 0 | -103 | 7708.23 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -228.1493 | 16 | 315.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:56 | 2009-10-12 03:04
2009-10-12 02:33 | 59.999 | 3781.2559 | 350 | -246.4331 | 16 |  | 10 | 0 | -103 | 7708.56 | 1 | 0 | 1 | 0 | 0 |  | 350 | -228.1493 | 16 | 316 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:04
2009-10-12 02:33 | 59.999 | 3780.595 | 350 | -246.4331 | 16 |  | 10 | 0 | -103 | 7708.89 | 1 | 0 | 1 | 0 | 0 |  | 350 | -235.129 | 16 | 316.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:04
2009-10-12 02:33 | 60.002 | 3783.092 | 350 | -246.4331 | 16 |  | 10 | 0 | -103 | 7709.22 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -235.129 | 16 | 317 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:05
2009-10-12 02:33 | 60.005 | 3783.8955 | 350 | -236.5535 | 16 |  | 10 | 0 | -103 | 7709.55 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -235.129 | 16 | 317.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:05
2009-10-12 02:33 | 60.007 | 3784.4209 | 350 | -236.5535 | 16 |  | 10 | 0 | -103 | 7709.88 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -235.129 | 16 | 318 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:05
2009-10-12 02:33 | 60.008 | 3785.7681 | 350 | -236.5535 | 16 |  | 10 | 0 | -103 | 7710.21 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -235.129 | 16 | 318.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:05
2009-10-12 02:33 | 60.011 | 3785.4626 | 350 | -236.5535 | 16 |  | 10 | 0 | -103 | 7710.54 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -246.4331 | 16 | 319 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:05
2009-10-12 02:33 | 60.014 | 3786.8503 | 350 | -236.5535 | 16 |  | 10 | 0 | -103 | 7710.87 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -246.4331 | 16 | 319.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:05
2009-10-12 02:33 | 60.017 | 3786.3042 | 350 | -230.2976 | 16 |  | 10 | 0 | -103 | 7711.2 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -246.4331 | 16 | 320 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:05
2009-10-12 02:33 | 60.019 | 3787.2593 | 350 | -230.2976 | 16 |  | 10 | 0 | -103 | 7711.53 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -246.4331 | 16 | 320.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:05
2009-10-12 02:33 | 60.021 | 3787.5159 | 350 | -230.2976 | 16 |  | 10 | 0 | -103 | 7711.86 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -246.4331 | 16 | 321 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:05
2009-10-12 02:33 | 60.017 | 3787.9551 | 350 | -230.2976 | 16 |  | 10 | 0 | -103 | 7712.19 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -236.5535 | 16 | 321.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:49 | 2009-10-12 02:57 | 2009-10-12 03:05
2009-10-12 02:33 | 60.017 | 3788.0303 | 350 | -230.2976 | 16 |  | 10 | 0 | -103 | 7712.52 | 1 | 1 | 1 | 0 | 0 |  | 350 | -236.5535 | 16 | 322 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:41 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:06
2009-10-12 02:33 | 60.019 | 3788.6067 | 350 | -231.1755 | 16 |  | 10 | 0 | -103 | 7712.85 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -236.5535 | 16 | 322.5 | 10 | 0 | 2009-10-12 02:33 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:06
2009-10-12 02:34 | 60.023 | 3789.2158 | 350 | -231.1755 | 16 |  | 10 | 0 | -103 | 7713.18 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -236.5535 | 16 | 323 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:06
2009-10-12 02:34 | 60.024 | 3787.5366 | 350 | -231.1755 | 16 |  | 10 | 0 | -103 | 7713.51 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -236.5535 | 16 | 323.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:06
2009-10-12 02:34 | 60.025 | 3785.8418 | 350 | -231.1755 | 16 |  | 10 | 0 | -103 | 7713.84 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -230.2976 | 16 | 324 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:06
2009-10-12 02:34 | 60.021 | 3786.0767 | 350 | -231.1755 | 16 |  | 10 | 0 | -103 | 7714.17 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -230.2976 | 16 | 324.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:06
2009-10-12 02:34 | 60.019 | 3787.9304 | 350 | -225.6176 | 16 |  | 10 | 0 | -103 | 7714.5 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -230.2976 | 16 | 325 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:06
2009-10-12 02:34 | 60.024 | 3788.7603 | 350 | -225.6176 | 16 |  | 10 | 0 | -103 | 7714.83 | 1 | 1 | 1 | 0.0049973 | 0.0049973 |  | 350 | -230.2976 | 16 | 325.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:06
2009-10-12 02:34 | 60.024 | 3786.8748 | 350 | -225.6176 | 16 |  | 10 | 0 | -103 | 7715.16 | 1 | 1 | 1 | 0 | 0 |  | 350 | -230.2976 | 16 | 326 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:06
2009-10-12 02:34 | 60.021 | 3786.5498 | 350 | -225.6176 | 16 |  | 10 | 0 | -103 | 7715.49 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -231.1755 | 16 | 326.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:06
2009-10-12 02:34 | 60.02 | 3787.3577 | 350 | -225.6176 | 16 |  | 10 | 0 | -103 | 7715.82 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -231.1755 | 16 | 327 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:07
2009-10-12 02:34 | 60.025 | 3785.0181 | 350 | -230.7344 | 16 |  | 10 | 0 | -103 | 7716.15 | 1 | 1 | 1 | 0.0050011 | 0.0050011 |  | 350 | -231.1755 | 16 | 327.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:58 | 2009-10-12 03:07
2009-10-12 02:34 | 60.024 | 3785.614 | 350 | -230.7344 | 16 |  | 10 | 0 | -103 | 7716.48 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -231.1755 | 16 | 328 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:59 | 2009-10-12 03:07
2009-10-12 02:34 | 60.02 | 3785.9492 | 350 | -230.7344 | 16 |  | 10 | 0 | -103 | 7716.81 | 1 | 1 | 1 | -0.0039978 | 0.0039978 |  | 350 | -231.1755 | 16 | 328.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:59 | 2009-10-12 03:07
2009-10-12 02:34 | 60.02 | 3785.8037 | 350 | -230.7344 | 16 |  | 10 | 0 | -103 | 7717.14 | 1 | 1 | 1 | 0 | 0 |  | 350 | -225.6176 | 16 | 329 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:50 | 2009-10-12 02:59 | 2009-10-12 03:07
2009-10-12 02:34 | 60.022 | 3786.8643 | 350 | -230.7344 | 16 |  | 10 | 0 | -103 | 7717.47 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -225.6176 | 16 | 329.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:51 | 2009-10-12 02:59 | 2009-10-12 03:07
2009-10-12 02:34 | 60.022 | 3786.8772 | 350 | -234.8471 | 16 |  | 10 | 0 | -103 | 7717.8 | 1 | 1 | 1 | 0 | 0 |  | 350 | -225.6176 | 16 | 330 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:51 | 2009-10-12 02:59 | 2009-10-12 03:07
2009-10-12 02:34 | 60.022 | 3785.2539 | 350 | -234.8471 | 16 |  | 10 | 0 | -103 | 7718.13 | 1 | 1 | 1 | 0 | 0 |  | 350 | -225.6176 | 16 | 330.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:51 | 2009-10-12 02:59 | 2009-10-12 03:07
2009-10-12 02:34 | 60.021 | 3785.7261 | 350 | -234.8471 | 16 |  | 10 | 0 | -103 | 7718.46 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -225.6176 | 16 | 331 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:51 | 2009-10-12 02:59 | 2009-10-12 03:07
2009-10-12 02:34 | 60.021 | 3786.3469 | 350 | -234.8471 | 16 |  | 10 | 0 | -103 | 7718.79 | 1 | 1 | 1 | 0 | 0 |  | 350 | -230.7344 | 16 | 331.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:51 | 2009-10-12 02:59 | 2009-10-12 03:07
2009-10-12 02:34 | 60.023 | 3785.821 | 350 | -234.8471 | 16 |  | 10 | 0 | -103 | 7719.12 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -230.7344 | 16 | 332 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:42 | 2009-10-12 02:51 | 2009-10-12 02:59 | 2009-10-12 03:08
2009-10-12 02:34 | 60.023 | 3785.7983 | 350 | -228.9609 | 16 |  | 10 | 0 | -103 | 7719.45 | 1 | 1 | 1 | 0 | 0 |  | 350 | -230.7344 | 16 | 332.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:43 | 2009-10-12 02:51 | 2009-10-12 02:59 | 2009-10-12 03:08
2009-10-12 02:34 | 60.022 | 3786.2842 | 350 | -228.9609 | 16 |  | 10 | 0 | -103 | 7719.78 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -230.7344 | 16 | 333 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:43 | 2009-10-12 02:51 | 2009-10-12 02:59 | 2009-10-12 03:08
2009-10-12 02:34 | 60.019 | 3786.9392 | 350 | -228.9609 | 16 |  | 10 | 0 | -103 | 7720.11 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -230.7344 | 16 | 333.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:43 | 2009-10-12 02:51 | 2009-10-12 02:59 | 2009-10-12 03:08
2009-10-12 02:34 | 60.016 | 3787.6274 | 350 | -228.9609 | 16 |  | 10 | 0 | -103 | 7720.44 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -234.8471 | 16 | 334 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:43 | 2009-10-12 02:51 | 2009-10-12 03:00 | 2009-10-12 03:08
2009-10-12 02:34 | 60.018 | 3789.4443 | 350 | -228.9609 | 16 |  | 10 | 0 | -103 | 7720.77 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -234.8471 | 16 | 334.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:43 | 2009-10-12 02:51 | 2009-10-12 03:00 | 2009-10-12 03:08
2009-10-12 02:34 | 60.018 | 3789.6733 | 350 | -231.1779 | 16 |  | 10 | 0 | -103 | 7721.1 | 1 | 1 | 1 | 0 | 0 |  | 350 | -234.8471 | 16 | 335 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:43 | 2009-10-12 02:51 | 2009-10-12 03:00 | 2009-10-12 03:08
2009-10-12 02:34 | 60.018 | 3789.4043 | 350 | -231.1779 | 16 |  | 10 | 0 | -103 | 7721.43 | 1 | 1 | 1 | 0 | 0 |  | 350 | -234.8471 | 16 | 335.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:43 | 2009-10-12 02:51 | 2009-10-12 03:00 | 2009-10-12 03:08
2009-10-12 02:34 | 60.019 | 3788.4788 | 350 | -231.1779 | 16 |  | 10 | 0 | -103 | 7721.76 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -234.8471 | 16 | 336 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:43 | 2009-10-12 02:51 | 2009-10-12 03:00 | 2009-10-12 03:08
2009-10-12 02:34 | 60.019 | 3789.1833 | 350 | -231.1779 | 16 |  | 10 | 0 | -103 | 7722.09 | 1 | 1 | 1 | 0 | 0 |  | 350 | -228.9609 | 16 | 336.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:43 | 2009-10-12 02:51 | 2009-10-12 03:00 | 2009-10-12 03:08
2009-10-12 02:34 | 60.016 | 3789.3689 | 350 | -231.1779 | 16 |  | 10 | 0 | -103 | 7722.42 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -228.9609 | 16 | 337 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:43 | 2009-10-12 02:52 | 2009-10-12 03:00 | 2009-10-12 03:09
2009-10-12 02:34 | 60.015 | 3789.0049 | 350 | -236.4893 | 16 |  | 10 | 0 | -103 | 7722.75 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -228.9609 | 16 | 337.5 | 10 | 0 | 2009-10-12 02:34 | 2009-10-12 02:43 | 2009-10-12 02:52 | 2009-10-12 03:00 | 2009-10-12 03:09
2009-10-12 02:35 | 60.016 | 3788.6646 | 350 | -236.4893 | 16 |  | 10 | 0 | -103 | 7723.08 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -228.9609 | 16 | 338 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:43 | 2009-10-12 02:52 | 2009-10-12 03:00 | 2009-10-12 03:09
2009-10-12 02:35 | 60.014 | 3788.9329 | 350 | -236.4893 | 16 |  | 10 | 0 | -103 | 7723.41 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -228.9609 | 16 | 338.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:43 | 2009-10-12 02:52 | 2009-10-12 03:00 | 2009-10-12 03:09
2009-10-12 02:35 | 60.013 | 3790.667 | 350 | -236.4893 | 16 |  | 10 | 0 | -103 | 7723.74 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -231.1779 | 16 | 339 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:43 | 2009-10-12 02:52 | 2009-10-12 03:00 | 2009-10-12 03:09
2009-10-12 02:35 | 60.012 | 3790.8052 | 350 | -236.4893 | 16 |  | 10 | 0 | -103 | 7724.07 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -231.1779 | 16 | 339.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:43 | 2009-10-12 02:52 | 2009-10-12 03:00 | 2009-10-12 03:09
2009-10-12 02:35 | 60.012 | 3790.4111 | 350 | -245.0389 | 16 |  | 10 | 0 | -103 | 7724.4 | 1 | 1 | 1 | 0 | 0 |  | 350 | -231.1779 | 16 | 340 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:43 | 2009-10-12 02:52 | 2009-10-12 03:01 | 2009-10-12 03:09
2009-10-12 02:35 | 60.01 | 3789.7686 | 350 | -245.0389 | 16 |  | 10 | 0 | -103 | 7724.73 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -231.1779 | 16 | 340.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:43 | 2009-10-12 02:52 | 2009-10-12 03:01 | 2009-10-12 03:09
2009-10-12 02:35 | 60.007 | 3791.5398 | 350 | -245.0389 | 16 |  | 10 | 0 | -103 | 7725.06 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -231.1779 | 16 | 341 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:43 | 2009-10-12 02:52 | 2009-10-12 03:01 | 2009-10-12 03:09
2009-10-12 02:35 | 60.007 | 3792.9453 | 350 | -245.0389 | 16 |  | 10 | 0 | -103 | 7725.39 | 1 | 1 | 1 | 0 | 0 |  | 350 | -236.4893 | 16 | 341.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:43 | 2009-10-12 02:52 | 2009-10-12 03:01 | 2009-10-12 03:09
2009-10-12 02:35 | 60.009 | 3791.0271 | 350 | -245.0389 | 16 |  | 10 | 0 | -103 | 7725.72 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -236.4893 | 16 | 342 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:43 | 2009-10-12 02:52 | 2009-10-12 03:01 | 2009-10-12 03:10
2009-10-12 02:35 | 60.009 | 3791.4431 | 350 | -223.6057 | 16 |  | 10 | 0 | -103 | 7726.05 | 1 | 1 | 1 | 0 | 0 |  | 350 | -236.4893 | 16 | 342.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:52 | 2009-10-12 03:01 | 2009-10-12 03:10
2009-10-12 02:35 | 60.01 | 3791.426 | 350 | -223.6057 | 16 |  | 10 | 0 | -103 | 7726.38 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -236.4893 | 16 | 343 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:52 | 2009-10-12 03:01 | 2009-10-12 03:10
2009-10-12 02:35 | 60.003 | 3790.603 | 350 | -223.6057 | 16 |  | 10 | 0 | -103 | 7726.71 | 1 | 1 | 1 | -0.007 | 0.007 |  | 350 | -236.4893 | 16 | 343.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:52 | 2009-10-12 03:01 | 2009-10-12 03:10
2009-10-12 02:35 | 59.999 | 3790.4573 | 350 | -223.6057 | 16 |  | 10 | 0 | -103 | 7727.04 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -245.0389 | 16 | 344 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:52 | 2009-10-12 03:01 | 2009-10-12 03:10
2009-10-12 02:35 | 59.995 | 3790.2163 | 350 | -223.6057 | 16 |  | 10 | 0 | -103 | 7727.37 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -245.0389 | 16 | 344.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:01 | 2009-10-12 03:10
2009-10-12 02:35 | 59.992 | 3789.585 | 350 | -231.1194 | 16 |  | 10 | 0 | -103 | 7727.7 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -245.0389 | 16 | 345 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:01 | 2009-10-12 03:10
2009-10-12 02:35 | 59.991 | 3788.457 | 350 | -231.1194 | 16 |  | 10 | 0 | -103 | 7728.03 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -245.0389 | 16 | 345.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:01 | 2009-10-12 03:10
2009-10-12 02:35 | 59.992 | 3788.105 | 350 | -231.1194 | 16 |  | 10 | 0 | -103 | 7728.36 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -245.0389 | 16 | 346 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:10
2009-10-12 02:35 | 59.992 | 3788.0571 | 350 | -231.1194 | 16 |  | 10 | 0 | -103 | 7728.69 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.6057 | 16 | 346.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:10
2009-10-12 02:35 | 59.988 | 3788.1895 | 350 | -231.1194 | 16 |  | 10 | 0 | -103 | 7729.02 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.6057 | 16 | 347 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:11
2009-10-12 02:35 | 59.986 | 3788.4973 | 350 | -237.2066 | 16 |  | 10 | 0 | -103 | 7729.35 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.6057 | 16 | 347.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:11
2009-10-12 02:35 | 59.985 | 3788.54 | 350 | -237.2066 | 16 |  | 10 | 0 | -103 | 7729.68 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.6057 | 16 | 348 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:11
2009-10-12 02:35 | 59.984 | 3788.5708 | 350 | -237.2066 | 16 |  | 10 | 0 | -103 | 7730.01 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.6057 | 16 | 348.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:11
2009-10-12 02:35 | 59.985 | 3788.1011 | 350 | -237.2066 | 16 |  | 10 | 0 | -103 | 7730.34 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -231.1194 | 16 | 349 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:11
2009-10-12 02:35 | 59.984 | 3787.1333 | 350 | -237.2066 | 16 |  | 10 | 0 | -103 | 7730.67 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -231.1194 | 16 | 349.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:11
2009-10-12 02:35 | 59.982 | 3786.4529 | 350 | -240.5164 | 16 |  | 10 | 0 | -103 | 7731 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -231.1194 | 16 | 350 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:11
2009-10-12 02:35 | 59.981 | 3787.7324 | 350 | -240.5164 | 16 |  | 10 | 0 | -103 | 7731.33 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -231.1194 | 16 | 350.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:11
2009-10-12 02:35 | 59.982 | 3788.8135 | 350 | -240.5164 | 16 |  | 10 | 0 | -103 | 7731.66 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -231.1194 | 16 | 351 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:11
2009-10-12 02:35 | 59.979 | 3789.2852 | 350 | -240.5164 | 16 |  | 10 | 0 | -103 | 7731.99 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -237.2066 | 16 | 351.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:53 | 2009-10-12 03:02 | 2009-10-12 03:11
2009-10-12 02:35 | 59.977 | 3788.2563 | 350 | -240.5164 | 16 |  | 10 | 0 | -103 | 7732.32 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -237.2066 | 16 | 352 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:44 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:12
2009-10-12 02:35 | 59.976 | 3788.4097 | 350 | -237.5661 | 16 |  | 10 | 0 | -103 | 7732.65 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -237.2066 | 16 | 352.5 | 10 | 0 | 2009-10-12 02:35 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:12
2009-10-12 02:36 | 59.976 | 3790.4673 | 350 | -237.5661 | 16 |  | 10 | 0 | -103 | 7732.98 | 1 | 0 | 1 | 0 | 0 |  | 350 | -237.2066 | 16 | 353 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:12
2009-10-12 02:36 | 59.979 | 3790.6646 | 350 | -237.5661 | 16 |  | 10 | 0 | -103 | 7733.31 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -237.2066 | 16 | 353.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:12
2009-10-12 02:36 | 59.982 | 3790.4204 | 350 | -237.5661 | 16 |  | 10 | 0 | -103 | 7733.64 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -240.5164 | 16 | 354 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:12
2009-10-12 02:36 | 59.978 | 3789.6738 | 350 | -237.5661 | 16 |  | 10 | 0 | -103 | 7733.97 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -240.5164 | 16 | 354.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:12
2009-10-12 02:36 | 59.976 | 3789.2671 | 350 | -231.5814 | 16 |  | 10 | 0 | -103 | 7734.3 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -240.5164 | 16 | 355 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:12
2009-10-12 02:36 | 59.974 | 3789.1479 | 350 | -231.5814 | 16 |  | 10 | 0 | -103 | 7734.63 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -240.5164 | 16 | 355.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:12
2009-10-12 02:36 | 59.976 | 3790.4304 | 350 | -231.5814 | 16 |  | 10 | 0 | -103 | 7734.96 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -240.5164 | 16 | 356 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:12
2009-10-12 02:36 | 59.977 | 3789.9143 | 350 | -231.5814 | 16 |  | 10 | 0 | -103 | 7735.29 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -237.5661 | 16 | 356.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:12
2009-10-12 02:36 | 59.977 | 3786.2432 | 350 | -231.5814 | 16 |  | 10 | 0 | -103 | 7735.62 | 1 | 0 | 1 | 0 | 0 |  | 350 | -237.5661 | 16 | 357 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:13
2009-10-12 02:36 | 59.975 | 3787.4421 | 350 | -235.8508 | 16 |  | 10 | 0 | -103 | 7735.95 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -237.5661 | 16 | 357.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:03 | 2009-10-12 03:13
2009-10-12 02:36 | 59.973 | 3788.9629 | 350 | -235.8508 | 16 |  | 10 | 0 | -103 | 7736.28 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -237.5661 | 16 | 358 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:04 | 2009-10-12 03:13
2009-10-12 02:36 | 59.969 | 3790.6016 | 350 | -235.8508 | 16 |  | 10 | 0 | -103 | 7736.61 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -237.5661 | 16 | 358.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:04 | 2009-10-12 03:13
2009-10-12 02:36 | 59.97 | 3791.877 | 350 | -235.8508 | 16 |  | 10 | 0 | -103 | 7736.94 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -231.5814 | 16 | 359 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:54 | 2009-10-12 03:04 | 2009-10-12 03:13
2009-10-12 02:36 | 59.971 | 3792.9106 | 350 | -235.8508 | 16 |  | 10 | 0 | -103 | 7737.27 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -231.5814 | 16 | 359.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:55 | 2009-10-12 03:04 | 2009-10-12 03:13
2009-10-12 02:36 | 59.973 | 3792.3113 | 350 | -233.56 | 16 |  | 10 | 0 | -103 | 7737.6 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -231.5814 | 16 | 360 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:55 | 2009-10-12 03:04 | 2009-10-12 03:13
2009-10-12 02:36 | 59.978 | 3789.125 | 350 | -233.56 | 16 |  | 10 | 0 | -103 | 7737.93 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -231.5814 | 16 | 360.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:55 | 2009-10-12 03:04 | 2009-10-12 03:13
2009-10-12 02:36 | 59.981 | 3788.0796 | 350 | -233.56 | 16 |  | 10 | 0 | -103 | 7738.26 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -231.5814 | 16 | 361 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:55 | 2009-10-12 03:04 | 2009-10-12 03:13
2009-10-12 02:36 | 59.978 | 3787.844 | 350 | -233.56 | 16 |  | 10 | 0 | -103 | 7738.59 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -235.8508 | 16 | 361.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:55 | 2009-10-12 03:04 | 2009-10-12 03:13
2009-10-12 02:36 | 59.975 | 3787.135 | 350 | -233.56 | 16 |  | 10 | 0 | -103 | 7738.92 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -235.8508 | 16 | 362 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:45 | 2009-10-12 02:55 | 2009-10-12 03:04 | 2009-10-12 03:14
2009-10-12 02:36 | 59.972 | 3787.1643 | 350 | -219.01 | 16 |  | 10 | 0 | -103 | 7739.25 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -235.8508 | 16 | 362.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:46 | 2009-10-12 02:55 | 2009-10-12 03:04 | 2009-10-12 03:14
2009-10-12 02:36 | 59.976 | 3786.9961 | 350 | -219.01 | 16 |  | 10 | 0 | -103 | 7739.58 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -235.8508 | 16 | 363 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:46 | 2009-10-12 02:55 | 2009-10-12 03:04 | 2009-10-12 03:14
2009-10-12 02:36 | 59.975 | 3787.4048 | 350 | -219.01 | 16 |  | 10 | 0 | -103 | 7739.91 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -235.8508 | 16 | 363.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:46 | 2009-10-12 02:55 | 2009-10-12 03:04 | 2009-10-12 03:14
2009-10-12 02:36 | 59.973 | 3786.4868 | 350 | -219.01 | 16 |  | 10 | 0 | -103 | 7740.24 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -233.56 | 16 | 364 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:46 | 2009-10-12 02:55 | 2009-10-12 03:05 | 2009-10-12 03:14
2009-10-12 02:36 | 59.969 | 3787.0791 | 350 | -219.01 | 16 |  | 10 | 0 | -103 | 7740.57 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -233.56 | 16 | 364.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:46 | 2009-10-12 02:55 | 2009-10-12 03:05 | 2009-10-12 03:14
2009-10-12 02:36 | 59.966 | 3789.2139 | 350 | -205.3389 | 16 |  | 10 | 0 | -103 | 7740.9 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -233.56 | 16 | 365 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:46 | 2009-10-12 02:55 | 2009-10-12 03:05 | 2009-10-12 03:14
2009-10-12 02:36 | 59.965 | 3790.5117 | 350 | -205.3389 | 16 |  | 10 | 0 | -103 | 7741.23 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -233.56 | 16 | 365.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:46 | 2009-10-12 02:55 | 2009-10-12 03:05 | 2009-10-12 03:14
2009-10-12 02:36 | 59.966 | 3791.2212 | 350 | -205.3389 | 16 |  | 10 | 0 | -103 | 7741.56 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -233.56 | 16 | 366 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:46 | 2009-10-12 02:55 | 2009-10-12 03:05 | 2009-10-12 03:14
2009-10-12 02:36 | 59.969 | 3792.2183 | 350 | -205.3389 | 16 |  | 10 | 0 | -103 | 7741.89 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -219.01 | 16 | 366.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:46 | 2009-10-12 02:55 | 2009-10-12 03:05 | 2009-10-12 03:14
2009-10-12 02:36 | 59.97 | 3790.9595 | 350 | -205.3389 | 16 |  | 10 | 0 | -103 | 7742.22 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -219.01 | 16 | 367 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:46 | 2009-10-12 02:56 | 2009-10-12 03:05 | 2009-10-12 03:15
2009-10-12 02:36 | 59.968 | 3788.8242 | 350 | -236.2854 | 16 |  | 10 | 0 | -103 | 7742.55 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -219.01 | 16 | 367.5 | 10 | 0 | 2009-10-12 02:36 | 2009-10-12 02:46 | 2009-10-12 02:56 | 2009-10-12 03:05 | 2009-10-12 03:15
2009-10-12 02:37 | 59.965 | 3789.0264 | 350 | -236.2854 | 16 |  | 10 | 0 | -103 | 7742.88 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -219.01 | 16 | 368 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:46 | 2009-10-12 02:56 | 2009-10-12 03:05 | 2009-10-12 03:15
2009-10-12 02:37 | 59.964 | 3789.1675 | 350 | -236.2854 | 16 |  | 10 | 0 | -103 | 7743.21 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -219.01 | 16 | 368.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:46 | 2009-10-12 02:56 | 2009-10-12 03:05 | 2009-10-12 03:15
2009-10-12 02:37 | 59.97 | 3787.394 | 350 | -236.2854 | 16 |  | 10 | 0 | -103 | 7743.54 | 1 | 0 | 1 | 0.0060005 | 0.0060005 |  | 350 | -205.3389 | 16 | 369 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:46 | 2009-10-12 02:56 | 2009-10-12 03:05 | 2009-10-12 03:15
2009-10-12 02:37 | 59.972 | 3785.6899 | 350 | -236.2854 | 16 |  | 10 | 0 | -103 | 7743.87 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -205.3389 | 16 | 369.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:46 | 2009-10-12 02:56 | 2009-10-12 03:05 | 2009-10-12 03:15
2009-10-12 02:37 | 59.967 | 3784.8306 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7744.2 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 350 | -205.3389 | 16 | 370 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:46 | 2009-10-12 02:56 | 2009-10-12 03:06 | 2009-10-12 03:15
2009-10-12 02:37 | 59.967 | 3785.0095 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7744.53 | 1 | 0 | 1 | 0 | 0 |  | 350 | -205.3389 | 16 | 370.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:46 | 2009-10-12 02:56 | 2009-10-12 03:06 | 2009-10-12 03:15
2009-10-12 02:37 | 59.969 | 3784.3203 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7744.86 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -205.3389 | 16 | 371 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:46 | 2009-10-12 02:56 | 2009-10-12 03:06 | 2009-10-12 03:15
2009-10-12 02:37 | 59.968 | 3782.8086 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7745.19 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -236.2854 | 16 | 371.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:46 | 2009-10-12 02:56 | 2009-10-12 03:06 | 2009-10-12 03:15
2009-10-12 02:37 | 59.969 | 3782.1099 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7745.52 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -236.2854 | 16 | 372 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:46 | 2009-10-12 02:56 | 2009-10-12 03:06 | 2009-10-12 03:16
2009-10-12 02:37 | 59.967 | 3779.3516 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7745.85 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -236.2854 | 16 | 372.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:56 | 2009-10-12 03:06 | 2009-10-12 03:16
2009-10-12 02:37 | 59.967 | 3779.0562 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7746.18 | 1 | 0 | 1 | 0 | 0 |  | 350 | -236.2854 | 16 | 373 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:56 | 2009-10-12 03:06 | 2009-10-12 03:16
2009-10-12 02:37 | 59.966 | 3778.6333 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7746.51 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -236.2854 | 16 | 373.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:56 | 2009-10-12 03:06 | 2009-10-12 03:16
2009-10-12 02:37 | 59.965 | 3779.2117 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7746.84 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 374 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:56 | 2009-10-12 03:06 | 2009-10-12 03:16
2009-10-12 02:37 | 59.971 | 3779.3347 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7747.17 | 1 | 0 | 1 | 0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 374.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:06 | 2009-10-12 03:16
2009-10-12 02:37 | 59.967 | 3776.4292 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7747.5 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 375 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:06 | 2009-10-12 03:16
2009-10-12 02:37 | 59.965 | 3775.6467 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7747.83 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 375.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:06 | 2009-10-12 03:16
2009-10-12 02:37 | 59.962 | 3776.5967 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7748.16 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 376 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:16
2009-10-12 02:37 | 59.964 | 3776.5591 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7748.49 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 376.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:16
2009-10-12 02:37 | 59.97 | 3776.0229 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7748.82 | 1 | 0 | 1 | 0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 377 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:17
2009-10-12 02:37 | 59.967 | 3773.1699 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7749.15 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 377.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:17
2009-10-12 02:37 | 59.969 | 3771.7305 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7749.48 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 378 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:17
2009-10-12 02:37 | 59.968 | 3768.793 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7749.81 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 378.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:17
2009-10-12 02:37 | 59.963 | 3768.5029 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7750.14 | 1 | 0 | 1 | -0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 379 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:17
2009-10-12 02:37 | 59.965 | 3768.9175 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7750.47 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 379.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:17
2009-10-12 02:37 | 59.97 | 3767.3662 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7750.8 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 380 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:17
2009-10-12 02:37 | 59.973 | 3764.7861 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7751.13 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 380.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:17
2009-10-12 02:37 | 59.968 | 3760.2954 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7751.46 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 381 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:17
2009-10-12 02:37 | 59.965 | 3759.5918 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7751.79 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 381.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:57 | 2009-10-12 03:07 | 2009-10-12 03:17
2009-10-12 02:37 | 59.968 | 3761.8938 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7752.12 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 382 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:47 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:18
2009-10-12 02:37 | 59.969 | 3761.7766 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7752.45 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 382.5 | 10 | 0 | 2009-10-12 02:37 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:18
2009-10-12 02:38 | 59.967 | 3760.5825 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7752.78 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 383 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:18
2009-10-12 02:38 | 59.964 | 3760.1575 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7753.11 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 383.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:18
2009-10-12 02:38 | 59.966 | 3759.781 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7753.44 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 384 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:18
2009-10-12 02:38 | 59.979 | 3759.4949 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7753.77 | 1 | 0 | 1 | 0.013 | 0.013 |  | 350 | -223.0157 | 16 | 384.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:18
2009-10-12 02:38 | 59.99 | 3757.7729 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7754.1 | 1 | 0 | 1 | 0.011002 | 0.011002 |  | 350 | -223.0157 | 16 | 385 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:18
2009-10-12 02:38 | 59.983 | 3753.2771 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7754.43 | 1 | 0 | 1 | -0.007 | 0.007 |  | 350 | -223.0157 | 16 | 385.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:18
2009-10-12 02:38 | 59.974 | 3753.0874 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7754.76 | 1 | 0 | 1 | -0.0090027 | 0.0090027 |  | 350 | -223.0157 | 16 | 386 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:18
2009-10-12 02:38 | 59.967 | 3751.6367 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7755.09 | 1 | 0 | 1 | -0.007 | 0.007 |  | 350 | -223.0157 | 16 | 386.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:18
2009-10-12 02:38 | 59.965 | 3753.751 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7755.42 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 387 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:19
2009-10-12 02:38 | 59.962 | 3758.2246 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7755.75 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 387.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:08 | 2009-10-12 03:19
2009-10-12 02:38 | 59.962 | 3759.2498 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7756.08 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 388 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:09 | 2009-10-12 03:19
2009-10-12 02:38 | 59.961 | 3758.041 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7756.41 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 388.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:09 | 2009-10-12 03:19
2009-10-12 02:38 | 59.961 | 3760.9648 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7756.74 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 389 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:58 | 2009-10-12 03:09 | 2009-10-12 03:19
2009-10-12 02:38 | 59.96 | 3762.0222 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7757.07 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 389.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:59 | 2009-10-12 03:09 | 2009-10-12 03:19
2009-10-12 02:38 | 59.963 | 3763.8223 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7757.4 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 390 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:59 | 2009-10-12 03:09 | 2009-10-12 03:19
2009-10-12 02:38 | 59.959 | 3763.1001 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7757.73 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 390.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:59 | 2009-10-12 03:09 | 2009-10-12 03:19
2009-10-12 02:38 | 59.956 | 3763.8582 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7758.06 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 391 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:59 | 2009-10-12 03:09 | 2009-10-12 03:19
2009-10-12 02:38 | 59.951 | 3764.1577 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7758.39 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 391.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:59 | 2009-10-12 03:09 | 2009-10-12 03:19
2009-10-12 02:38 | 59.953 | 3766.1267 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7758.72 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 392 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:48 | 2009-10-12 02:59 | 2009-10-12 03:09 | 2009-10-12 03:20
2009-10-12 02:38 | 59.954 | 3768.3389 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7759.05 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 392.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:49 | 2009-10-12 02:59 | 2009-10-12 03:09 | 2009-10-12 03:20
2009-10-12 02:38 | 59.957 | 3767.9722 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7759.38 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 393 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:49 | 2009-10-12 02:59 | 2009-10-12 03:09 | 2009-10-12 03:20
2009-10-12 02:38 | 59.956 | 3767.4375 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7759.71 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 393.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:49 | 2009-10-12 02:59 | 2009-10-12 03:09 | 2009-10-12 03:20
2009-10-12 02:38 | 59.961 | 3765.6064 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7760.04 | 1 | 0 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 394 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:49 | 2009-10-12 02:59 | 2009-10-12 03:10 | 2009-10-12 03:20
2009-10-12 02:38 | 59.963 | 3762.688 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7760.37 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 394.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:49 | 2009-10-12 02:59 | 2009-10-12 03:10 | 2009-10-12 03:20
2009-10-12 02:38 | 59.961 | 3761.5703 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7760.7 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 395 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:49 | 2009-10-12 02:59 | 2009-10-12 03:10 | 2009-10-12 03:20
2009-10-12 02:38 | 59.959 | 3761.9199 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7761.03 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 395.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:49 | 2009-10-12 02:59 | 2009-10-12 03:10 | 2009-10-12 03:20
2009-10-12 02:38 | 59.963 | 3759.627 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7761.36 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 396 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:49 | 2009-10-12 02:59 | 2009-10-12 03:10 | 2009-10-12 03:20
2009-10-12 02:38 | 59.963 | 3758.522 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7761.69 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 396.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:49 | 2009-10-12 02:59 | 2009-10-12 03:10 | 2009-10-12 03:20
2009-10-12 02:38 | 59.965 | 3752.4287 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7762.02 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 397 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:49 | 2009-10-12 03:00 | 2009-10-12 03:10 | 2009-10-12 03:21
2009-10-12 02:38 | 59.968 | 3750.1016 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7762.35 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 397.5 | 10 | 0 | 2009-10-12 02:38 | 2009-10-12 02:49 | 2009-10-12 03:00 | 2009-10-12 03:10 | 2009-10-12 03:21
2009-10-12 02:39 | 59.968 | 3753.8296 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7762.68 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 398 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:49 | 2009-10-12 03:00 | 2009-10-12 03:10 | 2009-10-12 03:21
2009-10-12 02:39 | 59.968 | 3753.5103 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7763.01 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 398.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:49 | 2009-10-12 03:00 | 2009-10-12 03:10 | 2009-10-12 03:21
2009-10-12 02:39 | 59.97 | 3753.5229 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7763.34 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 399 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:49 | 2009-10-12 03:00 | 2009-10-12 03:10 | 2009-10-12 03:21
2009-10-12 02:39 | 59.973 | 3752.7407 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7763.67 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 399.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:49 | 2009-10-12 03:00 | 2009-10-12 03:10 | 2009-10-12 03:21
2009-10-12 02:39 | 59.971 | 3753.1782 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7764 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 400 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:49 | 2009-10-12 03:00 | 2009-10-12 03:11 | 2009-10-12 03:21
2009-10-12 02:39 | 59.965 | 3752.729 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7764.33 | 1 | 0 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 400.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:49 | 2009-10-12 03:00 | 2009-10-12 03:11 | 2009-10-12 03:21
2009-10-12 02:39 | 59.967 | 3753.2905 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7764.66 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 401 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:49 | 2009-10-12 03:00 | 2009-10-12 03:11 | 2009-10-12 03:21
2009-10-12 02:39 | 59.967 | 3752.8716 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7764.99 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 401.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:49 | 2009-10-12 03:00 | 2009-10-12 03:11 | 2009-10-12 03:21
2009-10-12 02:39 | 59.972 | 3752.3586 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7765.32 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 402 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:49 | 2009-10-12 03:00 | 2009-10-12 03:11 | 2009-10-12 03:22
2009-10-12 02:39 | 59.976 | 3749.3979 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7765.65 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 402.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:00 | 2009-10-12 03:11 | 2009-10-12 03:22
2009-10-12 02:39 | 59.975 | 3747.4758 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7765.98 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 403 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:00 | 2009-10-12 03:11 | 2009-10-12 03:22
2009-10-12 02:39 | 59.969 | 3740.3704 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7766.31 | 1 | 0 | 1 | -0.0059967 | 0.0059967 |  | 350 | -223.0157 | 16 | 403.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:00 | 2009-10-12 03:11 | 2009-10-12 03:22
2009-10-12 02:39 | 59.973 | 3741.2852 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7766.64 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 404 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:00 | 2009-10-12 03:11 | 2009-10-12 03:22
2009-10-12 02:39 | 59.974 | 3746.6509 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7766.97 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 404.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:11 | 2009-10-12 03:22
2009-10-12 02:39 | 59.978 | 3745.7383 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7767.3 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 405 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:11 | 2009-10-12 03:22
2009-10-12 02:39 | 59.981 | 3743.3506 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7767.63 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 405.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:11 | 2009-10-12 03:22
2009-10-12 02:39 | 59.981 | 3741.6182 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7767.96 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 406 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:22
2009-10-12 02:39 | 59.981 | 3740.3064 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7768.29 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 406.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:22
2009-10-12 02:39 | 59.982 | 3738.4844 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7768.62 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 407 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:23
2009-10-12 02:39 | 59.982 | 3738.9014 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7768.95 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 407.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:23
2009-10-12 02:39 | 59.984 | 3737.4036 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7769.28 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 408 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:23
2009-10-12 02:39 | 59.982 | 3737.2732 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7769.61 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 408.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:23
2009-10-12 02:39 | 59.981 | 3736.3083 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7769.94 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 409 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:23
2009-10-12 02:39 | 59.979 | 3736.272 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7770.27 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 409.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:23
2009-10-12 02:39 | 59.98 | 3735.4482 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7770.6 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 410 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:23
2009-10-12 02:39 | 59.978 | 3735.6497 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7770.93 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 410.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:23
2009-10-12 02:39 | 59.978 | 3737.5405 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7771.26 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 411 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:23
2009-10-12 02:39 | 59.98 | 3738.012 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7771.59 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 411.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:01 | 2009-10-12 03:12 | 2009-10-12 03:23
2009-10-12 02:39 | 59.981 | 3736.7476 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7771.92 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 412 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:50 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:24
2009-10-12 02:39 | 59.98 | 3736.6931 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7772.25 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 412.5 | 10 | 0 | 2009-10-12 02:39 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:24
2009-10-12 02:40 | 59.978 | 3736.0674 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7772.58 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 413 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:24
2009-10-12 02:40 | 59.976 | 3736.0942 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7772.91 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 413.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:24
2009-10-12 02:40 | 59.972 | 3736.575 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7773.24 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 414 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:24
2009-10-12 02:40 | 59.971 | 3738.571 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7773.57 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 414.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:24
2009-10-12 02:40 | 59.969 | 3738.8748 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7773.9 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 415 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:24
2009-10-12 02:40 | 59.974 | 3738.9346 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7774.23 | 1 | 0 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 415.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:24
2009-10-12 02:40 | 59.975 | 3738.647 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7774.56 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 416 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:24
2009-10-12 02:40 | 59.976 | 3737.6841 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7774.89 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 416.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:24
2009-10-12 02:40 | 59.972 | 3737.3821 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7775.22 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 417 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:25
2009-10-12 02:40 | 59.969 | 3737.8921 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7775.55 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 417.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:13 | 2009-10-12 03:25
2009-10-12 02:40 | 59.971 | 3740.0168 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7775.88 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 418 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:14 | 2009-10-12 03:25
2009-10-12 02:40 | 59.974 | 3740.3289 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7776.21 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 418.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:14 | 2009-10-12 03:25
2009-10-12 02:40 | 59.972 | 3742.0527 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7776.54 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 419 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:02 | 2009-10-12 03:14 | 2009-10-12 03:25
2009-10-12 02:40 | 59.972 | 3742.4238 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7776.87 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 419.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:03 | 2009-10-12 03:14 | 2009-10-12 03:25
2009-10-12 02:40 | 59.972 | 3742.5244 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7777.2 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 420 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:03 | 2009-10-12 03:14 | 2009-10-12 03:25
2009-10-12 02:40 | 59.977 | 3742.2451 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7777.53 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 420.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:03 | 2009-10-12 03:14 | 2009-10-12 03:25
2009-10-12 02:40 | 59.982 | 3741.7231 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7777.86 | 1 | 0 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 421 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:03 | 2009-10-12 03:14 | 2009-10-12 03:25
2009-10-12 02:40 | 59.978 | 3740.0854 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7778.19 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 421.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:03 | 2009-10-12 03:14 | 2009-10-12 03:25
2009-10-12 02:40 | 59.976 | 3740.6292 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7778.52 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 422 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:51 | 2009-10-12 03:03 | 2009-10-12 03:14 | 2009-10-12 03:26
2009-10-12 02:40 | 59.973 | 3739.9644 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7778.85 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 422.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:52 | 2009-10-12 03:03 | 2009-10-12 03:14 | 2009-10-12 03:26
2009-10-12 02:40 | 59.974 | 3740.7751 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7779.18 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 423 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:52 | 2009-10-12 03:03 | 2009-10-12 03:14 | 2009-10-12 03:26
2009-10-12 02:40 | 59.977 | 3742.8325 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7779.51 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 423.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:52 | 2009-10-12 03:03 | 2009-10-12 03:14 | 2009-10-12 03:26
2009-10-12 02:40 | 59.977 | 3741.2678 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7779.84 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 424 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:52 | 2009-10-12 03:03 | 2009-10-12 03:15 | 2009-10-12 03:26
2009-10-12 02:40 | 59.978 | 3739.7761 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7780.17 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 424.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:52 | 2009-10-12 03:03 | 2009-10-12 03:15 | 2009-10-12 03:26
2009-10-12 02:40 | 59.979 | 3738.9658 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7780.5 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 425 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:52 | 2009-10-12 03:03 | 2009-10-12 03:15 | 2009-10-12 03:26
2009-10-12 02:40 | 59.981 | 3738.7061 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7780.83 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 425.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:52 | 2009-10-12 03:03 | 2009-10-12 03:15 | 2009-10-12 03:26
2009-10-12 02:40 | 59.977 | 3738.8787 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7781.16 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 426 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:52 | 2009-10-12 03:03 | 2009-10-12 03:15 | 2009-10-12 03:26
2009-10-12 02:40 | 59.974 | 3739.8596 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7781.49 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 426.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:52 | 2009-10-12 03:03 | 2009-10-12 03:15 | 2009-10-12 03:26
2009-10-12 02:40 | 59.971 | 3738.1016 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7781.82 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 427 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:52 | 2009-10-12 03:04 | 2009-10-12 03:15 | 2009-10-12 03:27
2009-10-12 02:40 | 59.971 | 3738.5579 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7782.15 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 427.5 | 10 | 0 | 2009-10-12 02:40 | 2009-10-12 02:52 | 2009-10-12 03:04 | 2009-10-12 03:15 | 2009-10-12 03:27
2009-10-12 02:41 | 59.971 | 3743.5068 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7782.48 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 428 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:52 | 2009-10-12 03:04 | 2009-10-12 03:15 | 2009-10-12 03:27
2009-10-12 02:41 | 59.972 | 3743.4187 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7782.81 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 428.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:52 | 2009-10-12 03:04 | 2009-10-12 03:15 | 2009-10-12 03:27
2009-10-12 02:41 | 59.968 | 3745.2507 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7783.14 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 429 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:52 | 2009-10-12 03:04 | 2009-10-12 03:15 | 2009-10-12 03:27
2009-10-12 02:41 | 59.966 | 3745.7441 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7783.47 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 429.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:52 | 2009-10-12 03:04 | 2009-10-12 03:15 | 2009-10-12 03:27
2009-10-12 02:41 | 59.966 | 3747.3396 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7783.8 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 430 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:52 | 2009-10-12 03:04 | 2009-10-12 03:16 | 2009-10-12 03:27
2009-10-12 02:41 | 59.971 | 3750.7002 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7784.13 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 430.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:52 | 2009-10-12 03:04 | 2009-10-12 03:16 | 2009-10-12 03:27
2009-10-12 02:41 | 59.973 | 3749.75 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7784.46 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 431 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:52 | 2009-10-12 03:04 | 2009-10-12 03:16 | 2009-10-12 03:27
2009-10-12 02:41 | 59.972 | 3746.2166 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7784.79 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 431.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:52 | 2009-10-12 03:04 | 2009-10-12 03:16 | 2009-10-12 03:27
2009-10-12 02:41 | 59.969 | 3744.6826 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7785.12 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 432 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:52 | 2009-10-12 03:04 | 2009-10-12 03:16 | 2009-10-12 03:28
2009-10-12 02:41 | 59.972 | 3743.7451 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7785.45 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 432.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:04 | 2009-10-12 03:16 | 2009-10-12 03:28
2009-10-12 02:41 | 59.974 | 3743.1489 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7785.78 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 433 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:04 | 2009-10-12 03:16 | 2009-10-12 03:28
2009-10-12 02:41 | 59.973 | 3740.2986 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7786.11 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 433.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:04 | 2009-10-12 03:16 | 2009-10-12 03:28
2009-10-12 02:41 | 59.97 | 3739.4526 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7786.44 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 434 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:04 | 2009-10-12 03:16 | 2009-10-12 03:28
2009-10-12 02:41 | 59.971 | 3733.376 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7786.77 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 434.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:16 | 2009-10-12 03:28
2009-10-12 02:41 | 59.974 | 3731.8296 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7787.1 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 435 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:16 | 2009-10-12 03:28
2009-10-12 02:41 | 59.982 | 3737.5825 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7787.43 | 1 | 0 | 1 | 0.0079994 | 0.0079994 |  | 350 | -223.0157 | 16 | 435.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:16 | 2009-10-12 03:28
2009-10-12 02:41 | 59.985 | 3736.2295 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7787.76 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 436 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:28
2009-10-12 02:41 | 59.985 | 3734.8967 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7788.09 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 436.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:28
2009-10-12 02:41 | 59.985 | 3733.4338 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7788.42 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 437 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:29
2009-10-12 02:41 | 59.987 | 3733.1152 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7788.75 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 437.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:29
2009-10-12 02:41 | 59.989 | 3730.5098 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7789.08 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 438 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:29
2009-10-12 02:41 | 59.989 | 3729.1802 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7789.41 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 438.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:29
2009-10-12 02:41 | 59.986 | 3725.4587 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7789.74 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 439 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:29
2009-10-12 02:41 | 59.987 | 3724.7847 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7790.07 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 439.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:29
2009-10-12 02:41 | 59.99 | 3720.1079 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7790.4 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 440 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:29
2009-10-12 02:41 | 59.994 | 3720.9382 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7790.73 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 440.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:29
2009-10-12 02:41 | 59.996 | 3725.6614 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7791.06 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 441 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:29
2009-10-12 02:41 | 60.001 | 3725.6768 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7791.39 | 1 | 1 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 441.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:05 | 2009-10-12 03:17 | 2009-10-12 03:29
2009-10-12 02:41 | 60.003 | 3727.7542 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7791.72 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 442 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:53 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:30
2009-10-12 02:41 | 60.004 | 3727.8247 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7792.05 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 442.5 | 10 | 0 | 2009-10-12 02:41 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:30
2009-10-12 02:42 | 60.006 | 3727.6833 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7792.38 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 443 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:30
2009-10-12 02:42 | 60.012 | 3727.2314 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7792.71 | 1 | 1 | 1 | 0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 443.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:30
2009-10-12 02:42 | 60.014 | 3725.0122 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7793.04 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 444 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:30
2009-10-12 02:42 | 60.019 | 3726.4463 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7793.37 | 1 | 1 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 444.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:30
2009-10-12 02:42 | 60.021 | 3726.0156 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7793.7 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 445 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:30
2009-10-12 02:42 | 60.025 | 3719.123 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7794.03 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 445.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:30
2009-10-12 02:42 | 60.026 | 3716.3745 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7794.36 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 446 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:30
2009-10-12 02:42 | 60.027 | 3717.3325 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7794.69 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 446.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:30
2009-10-12 02:42 | 60.029 | 3717.5598 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7795.02 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 447 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:31
2009-10-12 02:42 | 60.029 | 3717.1421 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7795.35 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 447.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:18 | 2009-10-12 03:31
2009-10-12 02:42 | 60.037 | 3715.166 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7795.68 | 1 | 1 | 1 | 0.0079994 | 0.0079994 |  | 350 | -223.0157 | 16 | 448 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:19 | 2009-10-12 03:31
2009-10-12 02:42 | 60.036 | 3713.6318 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7796.01 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 448.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:19 | 2009-10-12 03:31
2009-10-12 02:42 | 60.037 | 3710.2834 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7796.34 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 449 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:06 | 2009-10-12 03:19 | 2009-10-12 03:31
2009-10-12 02:42 | 60.037 | 3710.1577 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7796.67 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 449.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:07 | 2009-10-12 03:19 | 2009-10-12 03:31
2009-10-12 02:42 | 60.036 | 3699.3557 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7797 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 450 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:07 | 2009-10-12 03:19 | 2009-10-12 03:31
2009-10-12 02:42 | 60.041 | 3698.5911 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7797.33 | 1 | 1 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 450.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:07 | 2009-10-12 03:19 | 2009-10-12 03:31
2009-10-12 02:42 | 60.043 | 3704.5913 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7797.66 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 451 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:07 | 2009-10-12 03:19 | 2009-10-12 03:31
2009-10-12 02:42 | 60.044 | 3703.2754 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7797.99 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 451.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:07 | 2009-10-12 03:19 | 2009-10-12 03:31
2009-10-12 02:42 | 60.043 | 3702.4824 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7798.32 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 452 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:54 | 2009-10-12 03:07 | 2009-10-12 03:19 | 2009-10-12 03:32
2009-10-12 02:42 | 60.046 | 3701.3164 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7798.65 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 452.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:55 | 2009-10-12 03:07 | 2009-10-12 03:19 | 2009-10-12 03:32
2009-10-12 02:42 | 60.048 | 3700.8259 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7798.98 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 453 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:55 | 2009-10-12 03:07 | 2009-10-12 03:19 | 2009-10-12 03:32
2009-10-12 02:42 | 60.046 | 3699.5286 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7799.31 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 453.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:55 | 2009-10-12 03:07 | 2009-10-12 03:19 | 2009-10-12 03:32
2009-10-12 02:42 | 60.046 | 3699.7261 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7799.64 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 454 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:55 | 2009-10-12 03:07 | 2009-10-12 03:20 | 2009-10-12 03:32
2009-10-12 02:42 | 60.043 | 3690.0996 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7799.97 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 454.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:55 | 2009-10-12 03:07 | 2009-10-12 03:20 | 2009-10-12 03:32
2009-10-12 02:42 | 60.043 | 3690.4773 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7800.3 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 455 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:55 | 2009-10-12 03:07 | 2009-10-12 03:20 | 2009-10-12 03:32
2009-10-12 02:42 | 60.044 | 3696.8645 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7800.63 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 455.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:55 | 2009-10-12 03:07 | 2009-10-12 03:20 | 2009-10-12 03:32
2009-10-12 02:42 | 60.043 | 3696.8772 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7800.96 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 456 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:55 | 2009-10-12 03:07 | 2009-10-12 03:20 | 2009-10-12 03:32
2009-10-12 02:42 | 60.043 | 3696.1819 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7801.29 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 456.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:55 | 2009-10-12 03:07 | 2009-10-12 03:20 | 2009-10-12 03:32
2009-10-12 02:42 | 60.045 | 3696.5413 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7801.62 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 457 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:55 | 2009-10-12 03:08 | 2009-10-12 03:20 | 2009-10-12 03:33
2009-10-12 02:42 | 60.04 | 3696.9678 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7801.95 | 1 | 1 | 1 | -0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 457.5 | 10 | 0 | 2009-10-12 02:42 | 2009-10-12 02:55 | 2009-10-12 03:08 | 2009-10-12 03:20 | 2009-10-12 03:33
2009-10-12 02:43 | 60.041 | 3698.686 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7802.28 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 458 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:55 | 2009-10-12 03:08 | 2009-10-12 03:20 | 2009-10-12 03:33
2009-10-12 02:43 | 60.039 | 3699.6306 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7802.61 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 458.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:55 | 2009-10-12 03:08 | 2009-10-12 03:20 | 2009-10-12 03:33
2009-10-12 02:43 | 60.039 | 3698.7869 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7802.94 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 459 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:55 | 2009-10-12 03:08 | 2009-10-12 03:20 | 2009-10-12 03:33
2009-10-12 02:43 | 60.036 | 3699.7122 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7803.27 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 459.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:55 | 2009-10-12 03:08 | 2009-10-12 03:20 | 2009-10-12 03:33
2009-10-12 02:43 | 60.038 | 3700.1057 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7803.6 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 460 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:55 | 2009-10-12 03:08 | 2009-10-12 03:21 | 2009-10-12 03:33
2009-10-12 02:43 | 60.033 | 3699.968 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7803.93 | 1 | 1 | 1 | -0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 460.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:55 | 2009-10-12 03:08 | 2009-10-12 03:21 | 2009-10-12 03:33
2009-10-12 02:43 | 60.034 | 3701.1218 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7804.26 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 461 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:55 | 2009-10-12 03:08 | 2009-10-12 03:21 | 2009-10-12 03:33
2009-10-12 02:43 | 60.037 | 3701.8652 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7804.59 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 461.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:55 | 2009-10-12 03:08 | 2009-10-12 03:21 | 2009-10-12 03:33
2009-10-12 02:43 | 60.037 | 3701.6138 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7804.92 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 462 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:55 | 2009-10-12 03:08 | 2009-10-12 03:21 | 2009-10-12 03:34
2009-10-12 02:43 | 60.035 | 3701.9978 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7805.25 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 462.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:08 | 2009-10-12 03:21 | 2009-10-12 03:34
2009-10-12 02:43 | 60.03 | 3702.9126 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7805.58 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 463 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:08 | 2009-10-12 03:21 | 2009-10-12 03:34
2009-10-12 02:43 | 60.033 | 3703.9092 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7805.91 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 463.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:08 | 2009-10-12 03:21 | 2009-10-12 03:34
2009-10-12 02:43 | 60.036 | 3705.5225 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7806.24 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 464 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:08 | 2009-10-12 03:21 | 2009-10-12 03:34
2009-10-12 02:43 | 60.033 | 3704.9668 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7806.57 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 464.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:21 | 2009-10-12 03:34
2009-10-12 02:43 | 60.034 | 3704.0874 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7806.9 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 465 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:21 | 2009-10-12 03:34
2009-10-12 02:43 | 60.032 | 3702.7708 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7807.23 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 465.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:21 | 2009-10-12 03:34
2009-10-12 02:43 | 60.032 | 3703.7063 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7807.56 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 466 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:34
2009-10-12 02:43 | 60.034 | 3704.9053 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7807.89 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 466.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:34
2009-10-12 02:43 | 60.033 | 3705.4353 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7808.22 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 467 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:35
2009-10-12 02:43 | 60.037 | 3704.3601 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7808.55 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 467.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:35
2009-10-12 02:43 | 60.035 | 3702.5879 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7808.88 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 468 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:35
2009-10-12 02:43 | 60.035 | 3702.2043 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7809.21 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 468.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:35
2009-10-12 02:43 | 60.036 | 3701.9419 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7809.54 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 469 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:35
2009-10-12 02:43 | 60.039 | 3702.2505 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7809.87 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 469.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:35
2009-10-12 02:43 | 60.037 | 3703.3179 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7810.2 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 470 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:35
2009-10-12 02:43 | 60.039 | 3702.457 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7810.53 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 470.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:35
2009-10-12 02:43 | 60.036 | 3702.5249 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7810.86 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 471 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:35
2009-10-12 02:43 | 60.034 | 3703.2686 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7811.19 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 471.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:09 | 2009-10-12 03:22 | 2009-10-12 03:35
2009-10-12 02:43 | 60.038 | 3703.8435 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7811.52 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 472 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:56 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:36
2009-10-12 02:43 | 60.037 | 3702.8652 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7811.85 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 472.5 | 10 | 0 | 2009-10-12 02:43 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:36
2009-10-12 02:44 | 60.037 | 3702.5176 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7812.18 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 473 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:36
2009-10-12 02:44 | 60.037 | 3702.2795 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7812.51 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 473.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:36
2009-10-12 02:44 | 60.038 | 3692.427 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7812.84 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 474 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:36
2009-10-12 02:44 | 60.04 | 3692.178 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7813.17 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 474.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:36
2009-10-12 02:44 | 60.043 | 3700.2759 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7813.5 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 475 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:36
2009-10-12 02:44 | 60.045 | 3698.7554 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7813.83 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 475.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:36
2009-10-12 02:44 | 60.045 | 3697.7285 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7814.16 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 476 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:36
2009-10-12 02:44 | 60.042 | 3696.916 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7814.49 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 476.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:36
2009-10-12 02:44 | 60.043 | 3697.3684 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7814.82 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 477 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:37
2009-10-12 02:44 | 60.04 | 3697.3459 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7815.15 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 477.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:23 | 2009-10-12 03:37
2009-10-12 02:44 | 60.044 | 3698.4292 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7815.48 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 478 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:24 | 2009-10-12 03:37
2009-10-12 02:44 | 60.046 | 3694.7629 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7815.81 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 478.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:24 | 2009-10-12 03:37
2009-10-12 02:44 | 60.042 | 3693.5837 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7816.14 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 479 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:10 | 2009-10-12 03:24 | 2009-10-12 03:37
2009-10-12 02:44 | 60.034 | 3693.2407 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7816.47 | 1 | 1 | 1 | -0.0079994 | 0.0079994 |  | 350 | -223.0157 | 16 | 479.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:11 | 2009-10-12 03:24 | 2009-10-12 03:37
2009-10-12 02:44 | 60.039 | 3696.7983 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7816.8 | 1 | 1 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 480 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:11 | 2009-10-12 03:24 | 2009-10-12 03:37
2009-10-12 02:44 | 60.039 | 3699.3643 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7817.13 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 480.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:11 | 2009-10-12 03:24 | 2009-10-12 03:37
2009-10-12 02:44 | 60.036 | 3701.791 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7817.46 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 481 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:11 | 2009-10-12 03:24 | 2009-10-12 03:37
2009-10-12 02:44 | 60.037 | 3700.7083 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7817.79 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 481.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:11 | 2009-10-12 03:24 | 2009-10-12 03:37
2009-10-12 02:44 | 60.034 | 3700.7534 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7818.12 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 482 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:57 | 2009-10-12 03:11 | 2009-10-12 03:24 | 2009-10-12 03:38
2009-10-12 02:44 | 60.033 | 3702.1479 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7818.45 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 482.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:58 | 2009-10-12 03:11 | 2009-10-12 03:24 | 2009-10-12 03:38
2009-10-12 02:44 | 60.032 | 3705.2126 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7818.78 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 483 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:58 | 2009-10-12 03:11 | 2009-10-12 03:24 | 2009-10-12 03:38
2009-10-12 02:44 | 60.031 | 3707.521 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7819.11 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 483.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:58 | 2009-10-12 03:11 | 2009-10-12 03:24 | 2009-10-12 03:38
2009-10-12 02:44 | 60.033 | 3707.2866 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7819.44 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 484 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:58 | 2009-10-12 03:11 | 2009-10-12 03:25 | 2009-10-12 03:38
2009-10-12 02:44 | 60.027 | 3706.988 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7819.77 | 1 | 1 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 484.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:58 | 2009-10-12 03:11 | 2009-10-12 03:25 | 2009-10-12 03:38
2009-10-12 02:44 | 60.031 | 3707.3403 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7820.1 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 485 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:58 | 2009-10-12 03:11 | 2009-10-12 03:25 | 2009-10-12 03:38
2009-10-12 02:44 | 60.032 | 3707.9165 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7820.43 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 485.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:58 | 2009-10-12 03:11 | 2009-10-12 03:25 | 2009-10-12 03:38
2009-10-12 02:44 | 60.031 | 3707.3838 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7820.76 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 486 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:58 | 2009-10-12 03:11 | 2009-10-12 03:25 | 2009-10-12 03:38
2009-10-12 02:44 | 60.031 | 3706.8574 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7821.09 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 486.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:58 | 2009-10-12 03:11 | 2009-10-12 03:25 | 2009-10-12 03:38
2009-10-12 02:44 | 60.033 | 3707.6152 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7821.42 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 487 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:58 | 2009-10-12 03:12 | 2009-10-12 03:25 | 2009-10-12 03:39
2009-10-12 02:44 | 60.039 | 3706.8232 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7821.75 | 1 | 1 | 1 | 0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 487.5 | 10 | 0 | 2009-10-12 02:44 | 2009-10-12 02:58 | 2009-10-12 03:12 | 2009-10-12 03:25 | 2009-10-12 03:39
2009-10-12 02:45 | 60.039 | 3703.7461 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7822.08 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 488 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:58 | 2009-10-12 03:12 | 2009-10-12 03:25 | 2009-10-12 03:39
2009-10-12 02:45 | 60.038 | 3701.582 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7822.41 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 488.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:58 | 2009-10-12 03:12 | 2009-10-12 03:25 | 2009-10-12 03:39
2009-10-12 02:45 | 60.037 | 3700.8474 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7822.74 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 489 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:58 | 2009-10-12 03:12 | 2009-10-12 03:25 | 2009-10-12 03:39
2009-10-12 02:45 | 60.035 | 3701.2075 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7823.07 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 489.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:58 | 2009-10-12 03:12 | 2009-10-12 03:25 | 2009-10-12 03:39
2009-10-12 02:45 | 60.037 | 3702.2122 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7823.4 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 490 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:58 | 2009-10-12 03:12 | 2009-10-12 03:26 | 2009-10-12 03:39
2009-10-12 02:45 | 60.04 | 3701.6863 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7823.73 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 490.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:58 | 2009-10-12 03:12 | 2009-10-12 03:26 | 2009-10-12 03:39
2009-10-12 02:45 | 60.042 | 3700.3975 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7824.06 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 491 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:58 | 2009-10-12 03:12 | 2009-10-12 03:26 | 2009-10-12 03:39
2009-10-12 02:45 | 60.035 | 3699.6897 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7824.39 | 1 | 1 | 1 | -0.007 | 0.007 |  | 350 | -223.0157 | 16 | 491.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:58 | 2009-10-12 03:12 | 2009-10-12 03:26 | 2009-10-12 03:39
2009-10-12 02:45 | 60.036 | 3700.3665 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7824.72 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 492 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:58 | 2009-10-12 03:12 | 2009-10-12 03:26 | 2009-10-12 03:40
2009-10-12 02:45 | 60.04 | 3700.8271 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7825.05 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 492.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:12 | 2009-10-12 03:26 | 2009-10-12 03:40
2009-10-12 02:45 | 60.045 | 3700.6616 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7825.38 | 1 | 1 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 493 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:12 | 2009-10-12 03:26 | 2009-10-12 03:40
2009-10-12 02:45 | 60.045 | 3696.9351 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7825.71 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 493.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:12 | 2009-10-12 03:26 | 2009-10-12 03:40
2009-10-12 02:45 | 60.048 | 3695.6882 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7826.04 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 494 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:12 | 2009-10-12 03:26 | 2009-10-12 03:40
2009-10-12 02:45 | 60.042 | 3695.8186 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7826.37 | 1 | 1 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 494.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:26 | 2009-10-12 03:40
2009-10-12 02:45 | 60.044 | 3693.8242 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7826.7 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 495 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:26 | 2009-10-12 03:40
2009-10-12 02:45 | 60.044 | 3694.7991 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7827.03 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 495.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:26 | 2009-10-12 03:40
2009-10-12 02:45 | 60.044 | 3696.897 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7827.36 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 496 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:40
2009-10-12 02:45 | 60.041 | 3696.0227 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7827.69 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 496.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:40
2009-10-12 02:45 | 60.04 | 3697.5024 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7828.02 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 497 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:41
2009-10-12 02:45 | 60.04 | 3698.4243 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7828.35 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 497.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:41
2009-10-12 02:45 | 60.045 | 3699.4268 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7828.68 | 1 | 1 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 498 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:41
2009-10-12 02:45 | 60.044 | 3700.1768 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7829.01 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 498.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:41
2009-10-12 02:45 | 60.042 | 3699.8064 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7829.34 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 499 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:41
2009-10-12 02:45 | 60.039 | 3697.5774 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7829.67 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 499.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:41
2009-10-12 02:45 | 60.042 | 3697.6807 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7830 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 500 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:41
2009-10-12 02:45 | 60.042 | 3698.5073 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7830.33 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 500.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:41
2009-10-12 02:45 | 60.041 | 3698.3589 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7830.66 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 501 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:41
2009-10-12 02:45 | 60.038 | 3698.4658 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7830.99 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 501.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:13 | 2009-10-12 03:27 | 2009-10-12 03:41
2009-10-12 02:45 | 60.036 | 3699.0771 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7831.32 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 502 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 02:59 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:42
2009-10-12 02:45 | 60.037 | 3700.2622 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7831.65 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 502.5 | 10 | 0 | 2009-10-12 02:45 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:42
2009-10-12 02:46 | 60.039 | 3701.5918 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7831.98 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 503 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:42
2009-10-12 02:46 | 60.038 | 3700.9023 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7832.31 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 503.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:42
2009-10-12 02:46 | 60.04 | 3700.1428 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7832.64 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 504 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:42
2009-10-12 02:46 | 60.039 | 3700.27 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7832.97 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 504.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:42
2009-10-12 02:46 | 60.037 | 3701.1394 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7833.3 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 505 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:42
2009-10-12 02:46 | 60.038 | 3701.5857 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7833.63 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 505.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:42
2009-10-12 02:46 | 60.039 | 3700.2644 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7833.96 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 506 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:42
2009-10-12 02:46 | 60.04 | 3699.4585 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7834.29 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 506.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:42
2009-10-12 02:46 | 60.037 | 3699.7212 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7834.62 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 507 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:43
2009-10-12 02:46 | 60.037 | 3700.4575 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7834.95 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 507.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:28 | 2009-10-12 03:43
2009-10-12 02:46 | 60.037 | 3699.5051 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7835.28 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 508 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:29 | 2009-10-12 03:43
2009-10-12 02:46 | 60.039 | 3698.7944 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7835.61 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 508.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:29 | 2009-10-12 03:43
2009-10-12 02:46 | 60.038 | 3699.2161 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7835.94 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 509 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:14 | 2009-10-12 03:29 | 2009-10-12 03:43
2009-10-12 02:46 | 60.036 | 3699.4004 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7836.27 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 509.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:15 | 2009-10-12 03:29 | 2009-10-12 03:43
2009-10-12 02:46 | 60.035 | 3700.6614 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7836.6 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 510 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:15 | 2009-10-12 03:29 | 2009-10-12 03:43
2009-10-12 02:46 | 60.033 | 3702.1731 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7836.93 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 510.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:15 | 2009-10-12 03:29 | 2009-10-12 03:43
2009-10-12 02:46 | 60.031 | 3702.9675 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7837.26 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 511 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:15 | 2009-10-12 03:29 | 2009-10-12 03:43
2009-10-12 02:46 | 60.03 | 3705.1951 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7837.59 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 511.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:15 | 2009-10-12 03:29 | 2009-10-12 03:43
2009-10-12 02:46 | 60.032 | 3704.9517 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7837.92 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 512 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:00 | 2009-10-12 03:15 | 2009-10-12 03:29 | 2009-10-12 03:44
2009-10-12 02:46 | 60.032 | 3705.7751 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7838.25 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 512.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:01 | 2009-10-12 03:15 | 2009-10-12 03:29 | 2009-10-12 03:44
2009-10-12 02:46 | 60.037 | 3705.6213 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7838.58 | 1 | 1 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 513 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:01 | 2009-10-12 03:15 | 2009-10-12 03:29 | 2009-10-12 03:44
2009-10-12 02:46 | 60.042 | 3703.7441 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7838.91 | 1 | 1 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 513.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:01 | 2009-10-12 03:15 | 2009-10-12 03:29 | 2009-10-12 03:44
2009-10-12 02:46 | 60.041 | 3701.9812 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7839.24 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 514 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:01 | 2009-10-12 03:15 | 2009-10-12 03:30 | 2009-10-12 03:44
2009-10-12 02:46 | 60.036 | 3700.7563 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7839.57 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 514.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:01 | 2009-10-12 03:15 | 2009-10-12 03:30 | 2009-10-12 03:44
2009-10-12 02:46 | 60.031 | 3700.7471 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7839.9 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 515 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:01 | 2009-10-12 03:15 | 2009-10-12 03:30 | 2009-10-12 03:44
2009-10-12 02:46 | 60.032 | 3702.2126 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7840.23 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 515.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:01 | 2009-10-12 03:15 | 2009-10-12 03:30 | 2009-10-12 03:44
2009-10-12 02:46 | 60.031 | 3705.0593 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7840.56 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 516 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:01 | 2009-10-12 03:15 | 2009-10-12 03:30 | 2009-10-12 03:44
2009-10-12 02:46 | 60.034 | 3705.5137 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7840.89 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 516.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:01 | 2009-10-12 03:15 | 2009-10-12 03:30 | 2009-10-12 03:44
2009-10-12 02:46 | 60.034 | 3704.4487 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7841.22 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 517 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:01 | 2009-10-12 03:16 | 2009-10-12 03:30 | 2009-10-12 03:45
2009-10-12 02:46 | 60.032 | 3703.8308 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7841.55 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 517.5 | 10 | 0 | 2009-10-12 02:46 | 2009-10-12 03:01 | 2009-10-12 03:16 | 2009-10-12 03:30 | 2009-10-12 03:45
2009-10-12 02:47 | 60.038 | 3703.6196 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7841.88 | 1 | 1 | 1 | 0.0059967 | 0.0059967 |  | 350 | -223.0157 | 16 | 518 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:01 | 2009-10-12 03:16 | 2009-10-12 03:30 | 2009-10-12 03:45
2009-10-12 02:47 | 60.043 | 3702.7954 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7842.21 | 1 | 1 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 518.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:01 | 2009-10-12 03:16 | 2009-10-12 03:30 | 2009-10-12 03:45
2009-10-12 02:47 | 60.044 | 3701.4316 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7842.54 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 519 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:01 | 2009-10-12 03:16 | 2009-10-12 03:30 | 2009-10-12 03:45
2009-10-12 02:47 | 60.042 | 3697.3804 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7842.87 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 519.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:01 | 2009-10-12 03:16 | 2009-10-12 03:30 | 2009-10-12 03:45
2009-10-12 02:47 | 60.045 | 3696.2495 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7843.2 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 520 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:01 | 2009-10-12 03:16 | 2009-10-12 03:31 | 2009-10-12 03:45
2009-10-12 02:47 | 60.04 | 3696.302 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7843.53 | 1 | 1 | 1 | -0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 520.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:01 | 2009-10-12 03:16 | 2009-10-12 03:31 | 2009-10-12 03:45
2009-10-12 02:47 | 60.04 | 3693.5181 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7843.86 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 521 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:01 | 2009-10-12 03:16 | 2009-10-12 03:31 | 2009-10-12 03:45
2009-10-12 02:47 | 60.043 | 3693.5771 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7844.19 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 521.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:01 | 2009-10-12 03:16 | 2009-10-12 03:31 | 2009-10-12 03:45
2009-10-12 02:47 | 60.043 | 3695.197 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7844.52 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 522 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:01 | 2009-10-12 03:16 | 2009-10-12 03:31 | 2009-10-12 03:46
2009-10-12 02:47 | 60.041 | 3695.1855 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7844.85 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 522.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:16 | 2009-10-12 03:31 | 2009-10-12 03:46
2009-10-12 02:47 | 60.04 | 3693.7861 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7845.18 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 523 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:16 | 2009-10-12 03:31 | 2009-10-12 03:46
2009-10-12 02:47 | 60.038 | 3694.7534 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7845.51 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 523.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:16 | 2009-10-12 03:31 | 2009-10-12 03:46
2009-10-12 02:47 | 60.043 | 3694.9263 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7845.84 | 1 | 1 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 524 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:16 | 2009-10-12 03:31 | 2009-10-12 03:46
2009-10-12 02:47 | 60.044 | 3694.9377 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7846.17 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 524.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:31 | 2009-10-12 03:46
2009-10-12 02:47 | 60.042 | 3694.1594 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7846.5 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 525 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:31 | 2009-10-12 03:46
2009-10-12 02:47 | 60.036 | 3691.3301 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7846.83 | 1 | 1 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 525.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:31 | 2009-10-12 03:46
2009-10-12 02:47 | 60.043 | 3692.6863 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7847.16 | 1 | 1 | 1 | 0.007 | 0.007 |  | 350 | -223.0157 | 16 | 526 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:46
2009-10-12 02:47 | 60.041 | 3693.2383 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7847.49 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 526.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:46
2009-10-12 02:47 | 60.042 | 3693.3901 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7847.82 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 527 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:47
2009-10-12 02:47 | 60.043 | 3692.3569 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7848.15 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 527.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:47
2009-10-12 02:47 | 60.043 | 3690.9514 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7848.48 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 528 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:47
2009-10-12 02:47 | 60.036 | 3690.8362 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7848.81 | 1 | 1 | 1 | -0.007 | 0.007 |  | 350 | -223.0157 | 16 | 528.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:47
2009-10-12 02:47 | 60.039 | 3692.0422 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7849.14 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 529 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:47
2009-10-12 02:47 | 60.039 | 3693.1143 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7849.47 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 529.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:47
2009-10-12 02:47 | 60.037 | 3694.1172 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7849.8 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 530 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:47
2009-10-12 02:47 | 60.034 | 3695.2583 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7850.13 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 530.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:47
2009-10-12 02:47 | 60.035 | 3695.5808 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7850.46 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 531 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:47
2009-10-12 02:47 | 60.035 | 3695.9492 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7850.79 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 531.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:17 | 2009-10-12 03:32 | 2009-10-12 03:47
2009-10-12 02:47 | 60.035 | 3695.4912 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7851.12 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 532 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:02 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:48
2009-10-12 02:47 | 60.036 | 3696.3049 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7851.45 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 532.5 | 10 | 0 | 2009-10-12 02:47 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:48
2009-10-12 02:48 | 60.03 | 3696.4863 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7851.78 | 1 | 1 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 533 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:48
2009-10-12 02:48 | 60.03 | 3697.3357 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7852.11 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 533.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:48
2009-10-12 02:48 | 60.03 | 3699.1709 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7852.44 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 534 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:48
2009-10-12 02:48 | 60.031 | 3699.3569 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7852.77 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 534.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:48
2009-10-12 02:48 | 60.031 | 3699.2512 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7853.1 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 535 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:48
2009-10-12 02:48 | 60.032 | 3699.1172 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7853.43 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 535.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:48
2009-10-12 02:48 | 60.031 | 3699.1052 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7853.76 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 536 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:48
2009-10-12 02:48 | 60.032 | 3699.1265 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7854.09 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 536.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:48
2009-10-12 02:48 | 60.032 | 3698.9543 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7854.42 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 537 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:49
2009-10-12 02:48 | 60.032 | 3698.136 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7854.75 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 537.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:33 | 2009-10-12 03:49
2009-10-12 02:48 | 60.033 | 3698.2773 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7855.08 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 538 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:34 | 2009-10-12 03:49
2009-10-12 02:48 | 60.037 | 3697.4119 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7855.41 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 538.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:34 | 2009-10-12 03:49
2009-10-12 02:48 | 60.04 | 3695.9404 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7855.74 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 539 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:18 | 2009-10-12 03:34 | 2009-10-12 03:49
2009-10-12 02:48 | 60.039 | 3693.7358 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7856.07 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 539.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:19 | 2009-10-12 03:34 | 2009-10-12 03:49
2009-10-12 02:48 | 60.042 | 3693.2236 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7856.4 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 540 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:19 | 2009-10-12 03:34 | 2009-10-12 03:49
2009-10-12 02:48 | 60.036 | 3691.7585 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7856.73 | 1 | 1 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 540.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:19 | 2009-10-12 03:34 | 2009-10-12 03:49
2009-10-12 02:48 | 60.039 | 3691.9189 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7857.06 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 541 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:19 | 2009-10-12 03:34 | 2009-10-12 03:49
2009-10-12 02:48 | 60.041 | 3692.7983 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7857.39 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 541.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:19 | 2009-10-12 03:34 | 2009-10-12 03:49
2009-10-12 02:48 | 60.04 | 3691.5815 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7857.72 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 542 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:03 | 2009-10-12 03:19 | 2009-10-12 03:34 | 2009-10-12 03:50
2009-10-12 02:48 | 60.035 | 3692.3735 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7858.05 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 542.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:04 | 2009-10-12 03:19 | 2009-10-12 03:34 | 2009-10-12 03:50
2009-10-12 02:48 | 60.036 | 3693.3018 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7858.38 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 543 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:04 | 2009-10-12 03:19 | 2009-10-12 03:34 | 2009-10-12 03:50
2009-10-12 02:48 | 60.038 | 3694.7102 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7858.71 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 543.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:04 | 2009-10-12 03:19 | 2009-10-12 03:34 | 2009-10-12 03:50
2009-10-12 02:48 | 60.037 | 3694.3313 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7859.04 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 544 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:04 | 2009-10-12 03:19 | 2009-10-12 03:35 | 2009-10-12 03:50
2009-10-12 02:48 | 60.041 | 3693.8147 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7859.37 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 544.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:04 | 2009-10-12 03:19 | 2009-10-12 03:35 | 2009-10-12 03:50
2009-10-12 02:48 | 60.04 | 3693.6172 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7859.7 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 545 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:04 | 2009-10-12 03:19 | 2009-10-12 03:35 | 2009-10-12 03:50
2009-10-12 02:48 | 60.036 | 3694.324 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7860.03 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 545.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:04 | 2009-10-12 03:19 | 2009-10-12 03:35 | 2009-10-12 03:50
2009-10-12 02:48 | 60.033 | 3694.27 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7860.36 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 546 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:04 | 2009-10-12 03:19 | 2009-10-12 03:35 | 2009-10-12 03:50
2009-10-12 02:48 | 60.034 | 3694.6604 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7860.69 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 546.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:04 | 2009-10-12 03:19 | 2009-10-12 03:35 | 2009-10-12 03:50
2009-10-12 02:48 | 60.038 | 3693.7476 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7861.02 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 547 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:04 | 2009-10-12 03:20 | 2009-10-12 03:35 | 2009-10-12 03:51
2009-10-12 02:48 | 60.04 | 3692.5322 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7861.35 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 547.5 | 10 | 0 | 2009-10-12 02:48 | 2009-10-12 03:04 | 2009-10-12 03:20 | 2009-10-12 03:35 | 2009-10-12 03:51
2009-10-12 02:49 | 60.041 | 3691.4453 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7861.68 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 548 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:04 | 2009-10-12 03:20 | 2009-10-12 03:35 | 2009-10-12 03:51
2009-10-12 02:49 | 60.037 | 3691.0117 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7862.01 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 548.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:04 | 2009-10-12 03:20 | 2009-10-12 03:35 | 2009-10-12 03:51
2009-10-12 02:49 | 60.037 | 3691.7988 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7862.34 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 549 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:04 | 2009-10-12 03:20 | 2009-10-12 03:35 | 2009-10-12 03:51
2009-10-12 02:49 | 60.036 | 3693.0767 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7862.67 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 549.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:04 | 2009-10-12 03:20 | 2009-10-12 03:35 | 2009-10-12 03:51
2009-10-12 02:49 | 60.037 | 3693.7271 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7863 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 550 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:04 | 2009-10-12 03:20 | 2009-10-12 03:36 | 2009-10-12 03:51
2009-10-12 02:49 | 60.038 | 3693.1172 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7863.33 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 550.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:04 | 2009-10-12 03:20 | 2009-10-12 03:36 | 2009-10-12 03:51
2009-10-12 02:49 | 60.039 | 3692.6406 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7863.66 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 551 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:04 | 2009-10-12 03:20 | 2009-10-12 03:36 | 2009-10-12 03:51
2009-10-12 02:49 | 60.038 | 3688.1594 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7863.99 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 551.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:04 | 2009-10-12 03:20 | 2009-10-12 03:36 | 2009-10-12 03:51
2009-10-12 02:49 | 60.034 | 3689.0195 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7864.32 | 1 | 1 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 552 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:04 | 2009-10-12 03:20 | 2009-10-12 03:36 | 2009-10-12 03:52
2009-10-12 02:49 | 60.033 | 3688.2085 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7864.65 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 552.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:20 | 2009-10-12 03:36 | 2009-10-12 03:52
2009-10-12 02:49 | 60.031 | 3690.0918 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7864.98 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 553 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:20 | 2009-10-12 03:36 | 2009-10-12 03:52
2009-10-12 02:49 | 60.034 | 3693.1724 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7865.31 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 553.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:20 | 2009-10-12 03:36 | 2009-10-12 03:52
2009-10-12 02:49 | 60.029 | 3693.3208 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7865.64 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 554 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:20 | 2009-10-12 03:36 | 2009-10-12 03:52
2009-10-12 02:49 | 60.029 | 3694.5933 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7865.97 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 554.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:36 | 2009-10-12 03:52
2009-10-12 02:49 | 60.031 | 3695.2249 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7866.3 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 555 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:36 | 2009-10-12 03:52
2009-10-12 02:49 | 60.03 | 3694.6089 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7866.63 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 555.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:36 | 2009-10-12 03:52
2009-10-12 02:49 | 60.03 | 3693.4116 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7866.96 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 556 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:52
2009-10-12 02:49 | 60.026 | 3693.5085 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7867.29 | 1 | 1 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 556.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:52
2009-10-12 02:49 | 60.022 | 3696.0259 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7867.62 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 557 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:53
2009-10-12 02:49 | 60.021 | 3698.0122 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7867.95 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 557.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:53
2009-10-12 02:49 | 60.024 | 3699.0615 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7868.28 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 558 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:53
2009-10-12 02:49 | 60.023 | 3699.4143 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7868.61 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 558.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:53
2009-10-12 02:49 | 60.02 | 3698.9351 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7868.94 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 559 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:53
2009-10-12 02:49 | 60.021 | 3700.0837 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7869.27 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 559.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:53
2009-10-12 02:49 | 60.023 | 3700.5442 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7869.6 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 560 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:53
2009-10-12 02:49 | 60.025 | 3700.4858 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7869.93 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 560.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:53
2009-10-12 02:49 | 60.026 | 3698.5957 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7870.26 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 561 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:53
2009-10-12 02:49 | 60.026 | 3697.9607 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7870.59 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 561.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:21 | 2009-10-12 03:37 | 2009-10-12 03:53
2009-10-12 02:49 | 60.025 | 3699.9138 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7870.92 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 562 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:05 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:54
2009-10-12 02:49 | 60.024 | 3700.8025 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7871.25 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 562.5 | 10 | 0 | 2009-10-12 02:49 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:54
2009-10-12 02:50 | 60.024 | 3701.3013 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7871.58 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 563 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:54
2009-10-12 02:50 | 60.025 | 3701.4502 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7871.91 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 563.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:54
2009-10-12 02:50 | 60.023 | 3701.3486 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7872.24 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 564 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:54
2009-10-12 02:50 | 60.023 | 3701.0938 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7872.57 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 564.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:54
2009-10-12 02:50 | 60.022 | 3701.7017 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7872.9 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 565 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:54
2009-10-12 02:50 | 60.026 | 3702.0703 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7873.23 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 565.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:54
2009-10-12 02:50 | 60.029 | 3701.9648 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7873.56 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 566 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:54
2009-10-12 02:50 | 60.026 | 3700.2688 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7873.89 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 566.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:54
2009-10-12 02:50 | 60.024 | 3700.2412 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7874.22 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 567 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:55
2009-10-12 02:50 | 60.021 | 3701.0898 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7874.55 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 567.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:38 | 2009-10-12 03:55
2009-10-12 02:50 | 60.025 | 3701.2681 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7874.88 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 568 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:39 | 2009-10-12 03:55
2009-10-12 02:50 | 60.025 | 3701.2046 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7875.21 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 568.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:39 | 2009-10-12 03:55
2009-10-12 02:50 | 60.025 | 3700.5874 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7875.54 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 569 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:22 | 2009-10-12 03:39 | 2009-10-12 03:55
2009-10-12 02:50 | 60.023 | 3700.5317 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7875.87 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 569.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:23 | 2009-10-12 03:39 | 2009-10-12 03:55
2009-10-12 02:50 | 60.026 | 3700.1768 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7876.2 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 570 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:23 | 2009-10-12 03:39 | 2009-10-12 03:55
2009-10-12 02:50 | 60.024 | 3700.2954 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7876.53 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 570.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:23 | 2009-10-12 03:39 | 2009-10-12 03:55
2009-10-12 02:50 | 60.022 | 3700.2773 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7876.86 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 571 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:23 | 2009-10-12 03:39 | 2009-10-12 03:55
2009-10-12 02:50 | 60.023 | 3700.8408 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7877.19 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 571.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:23 | 2009-10-12 03:39 | 2009-10-12 03:55
2009-10-12 02:50 | 60.026 | 3700.8628 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7877.52 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 572 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:06 | 2009-10-12 03:23 | 2009-10-12 03:39 | 2009-10-12 03:56
2009-10-12 02:50 | 60.025 | 3700.2603 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7877.85 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 572.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:07 | 2009-10-12 03:23 | 2009-10-12 03:39 | 2009-10-12 03:56
2009-10-12 02:50 | 60.02 | 3700.0525 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7878.18 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 573 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:07 | 2009-10-12 03:23 | 2009-10-12 03:39 | 2009-10-12 03:56
2009-10-12 02:50 | 60.02 | 3699.9255 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7878.51 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 573.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:07 | 2009-10-12 03:23 | 2009-10-12 03:39 | 2009-10-12 03:56
2009-10-12 02:50 | 60.019 | 3700.9648 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7878.84 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 574 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:07 | 2009-10-12 03:23 | 2009-10-12 03:40 | 2009-10-12 03:56
2009-10-12 02:50 | 60.015 | 3702.5811 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7879.17 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 574.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:07 | 2009-10-12 03:23 | 2009-10-12 03:40 | 2009-10-12 03:56
2009-10-12 02:50 | 60.016 | 3703.5161 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7879.5 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 575 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:07 | 2009-10-12 03:23 | 2009-10-12 03:40 | 2009-10-12 03:56
2009-10-12 02:50 | 60.017 | 3703.8237 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7879.83 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 575.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:07 | 2009-10-12 03:23 | 2009-10-12 03:40 | 2009-10-12 03:56
2009-10-12 02:50 | 60.015 | 3703.6724 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7880.16 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 576 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:07 | 2009-10-12 03:23 | 2009-10-12 03:40 | 2009-10-12 03:56
2009-10-12 02:50 | 60.015 | 3703.6895 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7880.49 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 576.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:07 | 2009-10-12 03:23 | 2009-10-12 03:40 | 2009-10-12 03:56
2009-10-12 02:50 | 60.017 | 3703.0034 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7880.82 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 577 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:07 | 2009-10-12 03:24 | 2009-10-12 03:40 | 2009-10-12 03:57
2009-10-12 02:50 | 60.017 | 3702.9214 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7881.15 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 577.5 | 10 | 0 | 2009-10-12 02:50 | 2009-10-12 03:07 | 2009-10-12 03:24 | 2009-10-12 03:40 | 2009-10-12 03:57
2009-10-12 02:51 | 60.012 | 3702.9995 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7881.48 | 1 | 1 | 1 | -0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 578 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:07 | 2009-10-12 03:24 | 2009-10-12 03:40 | 2009-10-12 03:57
2009-10-12 02:51 | 60.01 | 3703.1667 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7881.81 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 578.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:07 | 2009-10-12 03:24 | 2009-10-12 03:40 | 2009-10-12 03:57
2009-10-12 02:51 | 60.008 | 3703.9182 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7882.14 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 579 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:07 | 2009-10-12 03:24 | 2009-10-12 03:40 | 2009-10-12 03:57
2009-10-12 02:51 | 60.002 | 3703.6157 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7882.47 | 1 | 1 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 579.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:07 | 2009-10-12 03:24 | 2009-10-12 03:40 | 2009-10-12 03:57
2009-10-12 02:51 | 59.999 | 3703.7754 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7882.8 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 580 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:07 | 2009-10-12 03:24 | 2009-10-12 03:41 | 2009-10-12 03:57
2009-10-12 02:51 | 59.999 | 3703.751 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7883.13 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 580.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:07 | 2009-10-12 03:24 | 2009-10-12 03:41 | 2009-10-12 03:57
2009-10-12 02:51 | 60.002 | 3701.5337 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7883.46 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 581 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:07 | 2009-10-12 03:24 | 2009-10-12 03:41 | 2009-10-12 03:57
2009-10-12 02:51 | 60.003 | 3700.6167 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7883.79 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 581.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:07 | 2009-10-12 03:24 | 2009-10-12 03:41 | 2009-10-12 03:57
2009-10-12 02:51 | 60.004 | 3700.8804 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7884.12 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 582 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:07 | 2009-10-12 03:24 | 2009-10-12 03:41 | 2009-10-12 03:58
2009-10-12 02:51 | 60.001 | 3700.6252 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7884.45 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 582.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:24 | 2009-10-12 03:41 | 2009-10-12 03:58
2009-10-12 02:51 | 59.996 | 3701.3889 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7884.78 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 583 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:24 | 2009-10-12 03:41 | 2009-10-12 03:58
2009-10-12 02:51 | 59.993 | 3701.7366 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7885.11 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 583.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:24 | 2009-10-12 03:41 | 2009-10-12 03:58
2009-10-12 02:51 | 59.992 | 3700.6714 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7885.44 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 584 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:24 | 2009-10-12 03:41 | 2009-10-12 03:58
2009-10-12 02:51 | 59.989 | 3700.8264 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7885.77 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 584.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:41 | 2009-10-12 03:58
2009-10-12 02:51 | 59.987 | 3700.9771 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7886.1 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 585 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:41 | 2009-10-12 03:58
2009-10-12 02:51 | 59.985 | 3700.7 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7886.43 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 585.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:41 | 2009-10-12 03:58
2009-10-12 02:51 | 59.985 | 3699.8538 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7886.76 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 586 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:58
2009-10-12 02:51 | 59.986 | 3700.2373 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7887.09 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 586.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:58
2009-10-12 02:51 | 59.984 | 3700.3423 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7887.42 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 587 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:59
2009-10-12 02:51 | 59.981 | 3700.7698 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7887.75 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 587.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:59
2009-10-12 02:51 | 59.98 | 3700.7893 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7888.08 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 588 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:59
2009-10-12 02:51 | 59.977 | 3701.6252 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7888.41 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 588.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:59
2009-10-12 02:51 | 59.975 | 3703.1658 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7888.74 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 589 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:59
2009-10-12 02:51 | 59.976 | 3704.187 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7889.07 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 589.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:59
2009-10-12 02:51 | 59.972 | 3704.7847 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7889.4 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 590 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:59
2009-10-12 02:51 | 59.974 | 3705.8105 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7889.73 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 590.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:59
2009-10-12 02:51 | 59.977 | 3706.958 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7890.06 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 591 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:59
2009-10-12 02:51 | 59.975 | 3706.688 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7890.39 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 591.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:25 | 2009-10-12 03:42 | 2009-10-12 03:59
2009-10-12 02:51 | 59.973 | 3706.543 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7890.72 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 592 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:08 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:00
2009-10-12 02:51 | 59.971 | 3706.2571 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7891.05 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 592.5 | 10 | 0 | 2009-10-12 02:51 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:00
2009-10-12 02:52 | 59.971 | 3707.0266 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7891.38 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 593 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:00
2009-10-12 02:52 | 59.976 | 3710.1182 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7891.71 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 593.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:00
2009-10-12 02:52 | 59.979 | 3710.5312 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7892.04 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 594 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:00
2009-10-12 02:52 | 59.98 | 3708.7007 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7892.37 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 594.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:00
2009-10-12 02:52 | 59.979 | 3708.0181 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7892.7 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 595 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:00
2009-10-12 02:52 | 59.982 | 3706.9424 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7893.03 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 595.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:00
2009-10-12 02:52 | 59.982 | 3706.3425 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7893.36 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 596 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:00
2009-10-12 02:52 | 59.983 | 3706.1255 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7893.69 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 596.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:00
2009-10-12 02:52 | 59.981 | 3706.3105 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7894.02 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 597 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:01
2009-10-12 02:52 | 59.979 | 3706.1187 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7894.35 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 597.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:43 | 2009-10-12 04:01
2009-10-12 02:52 | 59.978 | 3706.1904 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7894.68 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 598 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:44 | 2009-10-12 04:01
2009-10-12 02:52 | 59.976 | 3707.7209 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7895.01 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 598.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:44 | 2009-10-12 04:01
2009-10-12 02:52 | 59.978 | 3709.4089 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7895.34 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 599 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:26 | 2009-10-12 03:44 | 2009-10-12 04:01
2009-10-12 02:52 | 59.977 | 3708.9714 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7895.67 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 599.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:27 | 2009-10-12 03:44 | 2009-10-12 04:01
2009-10-12 02:52 | 59.976 | 3708.5305 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7896 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 600 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:27 | 2009-10-12 03:44 | 2009-10-12 04:01
2009-10-12 02:52 | 59.978 | 3708.0708 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7896.33 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 600.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:27 | 2009-10-12 03:44 | 2009-10-12 04:01
2009-10-12 02:52 | 59.975 | 3707.24 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7896.66 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 601 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:27 | 2009-10-12 03:44 | 2009-10-12 04:01
2009-10-12 02:52 | 59.971 | 3709.2126 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7896.99 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 601.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:27 | 2009-10-12 03:44 | 2009-10-12 04:01
2009-10-12 02:52 | 59.97 | 3709.9612 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7897.32 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 602 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:09 | 2009-10-12 03:27 | 2009-10-12 03:44 | 2009-10-12 04:02
2009-10-12 02:52 | 59.97 | 3711.75 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7897.65 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 602.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:10 | 2009-10-12 03:27 | 2009-10-12 03:44 | 2009-10-12 04:02
2009-10-12 02:52 | 59.971 | 3711.9805 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7897.98 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 603 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:10 | 2009-10-12 03:27 | 2009-10-12 03:44 | 2009-10-12 04:02
2009-10-12 02:52 | 59.99 | 3710.6953 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7898.31 | 1 | 0 | 1 | 0.019001 | 0.019001 |  | 350 | -223.0157 | 16 | 603.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:10 | 2009-10-12 03:27 | 2009-10-12 03:44 | 2009-10-12 04:02
2009-10-12 02:52 | 59.998 | 3707.8667 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7898.64 | 1 | 0 | 1 | 0.0079994 | 0.0079994 |  | 350 | -223.0157 | 16 | 604 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:10 | 2009-10-12 03:27 | 2009-10-12 03:45 | 2009-10-12 04:02
2009-10-12 02:52 | 59.999 | 3704.9119 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7898.97 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 604.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:10 | 2009-10-12 03:27 | 2009-10-12 03:45 | 2009-10-12 04:02
2009-10-12 02:52 | 59.999 | 3705.6392 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7899.3 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 605 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:10 | 2009-10-12 03:27 | 2009-10-12 03:45 | 2009-10-12 04:02
2009-10-12 02:52 | 59.998 | 3703.7869 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7899.63 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 605.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:10 | 2009-10-12 03:27 | 2009-10-12 03:45 | 2009-10-12 04:02
2009-10-12 02:52 | 59.999 | 3703.1909 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7899.96 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 606 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:10 | 2009-10-12 03:27 | 2009-10-12 03:45 | 2009-10-12 04:02
2009-10-12 02:52 | 60.003 | 3702.0706 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7900.29 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 606.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:10 | 2009-10-12 03:27 | 2009-10-12 03:45 | 2009-10-12 04:02
2009-10-12 02:52 | 60.005 | 3699.51 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7900.62 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 607 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:10 | 2009-10-12 03:28 | 2009-10-12 03:45 | 2009-10-12 04:03
2009-10-12 02:52 | 60.005 | 3698.658 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7900.95 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 607.5 | 10 | 0 | 2009-10-12 02:52 | 2009-10-12 03:10 | 2009-10-12 03:28 | 2009-10-12 03:45 | 2009-10-12 04:03
2009-10-12 02:53 | 60.01 | 3698.1367 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7901.28 | 1 | 1 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 608 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:10 | 2009-10-12 03:28 | 2009-10-12 03:45 | 2009-10-12 04:03
2009-10-12 02:53 | 60.013 | 3697.8821 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7901.61 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 608.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:10 | 2009-10-12 03:28 | 2009-10-12 03:45 | 2009-10-12 04:03
2009-10-12 02:53 | 60.02 | 3698.6682 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7901.94 | 1 | 1 | 1 | 0.007 | 0.007 |  | 350 | -223.0157 | 16 | 609 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:10 | 2009-10-12 03:28 | 2009-10-12 03:45 | 2009-10-12 04:03
2009-10-12 02:53 | 60.022 | 3698.6045 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7902.27 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 609.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:10 | 2009-10-12 03:28 | 2009-10-12 03:45 | 2009-10-12 04:03
2009-10-12 02:53 | 60.024 | 3697.8684 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7902.6 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 610 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:10 | 2009-10-12 03:28 | 2009-10-12 03:46 | 2009-10-12 04:03
2009-10-12 02:53 | 60.025 | 3694.6719 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7902.93 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 610.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:10 | 2009-10-12 03:28 | 2009-10-12 03:46 | 2009-10-12 04:03
2009-10-12 02:53 | 60.025 | 3693.9121 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7903.26 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 611 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:10 | 2009-10-12 03:28 | 2009-10-12 03:46 | 2009-10-12 04:03
2009-10-12 02:53 | 60.024 | 3693.4177 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7903.59 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 611.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:10 | 2009-10-12 03:28 | 2009-10-12 03:46 | 2009-10-12 04:03
2009-10-12 02:53 | 60.023 | 3688.3013 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7903.92 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 612 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:10 | 2009-10-12 03:28 | 2009-10-12 03:46 | 2009-10-12 04:04
2009-10-12 02:53 | 60.029 | 3688.021 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7904.25 | 1 | 1 | 1 | 0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 612.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:28 | 2009-10-12 03:46 | 2009-10-12 04:04
2009-10-12 02:53 | 60.029 | 3689.1431 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7904.58 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 613 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:28 | 2009-10-12 03:46 | 2009-10-12 04:04
2009-10-12 02:53 | 60.029 | 3688.2368 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7904.91 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 613.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:28 | 2009-10-12 03:46 | 2009-10-12 04:04
2009-10-12 02:53 | 60.028 | 3687.8779 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7905.24 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 614 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:28 | 2009-10-12 03:46 | 2009-10-12 04:04
2009-10-12 02:53 | 60.028 | 3687.0264 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7905.57 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 614.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:46 | 2009-10-12 04:04
2009-10-12 02:53 | 60.031 | 3686.6831 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7905.9 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 615 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:46 | 2009-10-12 04:04
2009-10-12 02:53 | 60.032 | 3685.2756 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7906.23 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 615.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:46 | 2009-10-12 04:04
2009-10-12 02:53 | 60.033 | 3685.5762 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7906.56 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 616 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:04
2009-10-12 02:53 | 60.031 | 3685.9849 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7906.89 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 616.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:04
2009-10-12 02:53 | 60.03 | 3686.418 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7907.22 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 617 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:05
2009-10-12 02:53 | 60.022 | 3687.1589 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7907.55 | 1 | 1 | 1 | -0.0079994 | 0.0079994 |  | 350 | -223.0157 | 16 | 617.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:05
2009-10-12 02:53 | 60.021 | 3687.873 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7907.88 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 618 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:05
2009-10-12 02:53 | 60.019 | 3688.9971 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7908.21 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 618.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:05
2009-10-12 02:53 | 60.017 | 3690.4258 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7908.54 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 619 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:05
2009-10-12 02:53 | 60.017 | 3690.7756 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7908.87 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 619.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:05
2009-10-12 02:53 | 60.017 | 3692.7153 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7909.2 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 620 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:05
2009-10-12 02:53 | 60.016 | 3692.5776 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7909.53 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 620.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:05
2009-10-12 02:53 | 60.015 | 3692.4617 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7909.86 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 621 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:05
2009-10-12 02:53 | 60.015 | 3693.1731 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7910.19 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 621.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:29 | 2009-10-12 03:47 | 2009-10-12 04:05
2009-10-12 02:53 | 60.012 | 3693.2488 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7910.52 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 622 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:11 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:06
2009-10-12 02:53 | 60.009 | 3693.7434 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7910.85 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 622.5 | 10 | 0 | 2009-10-12 02:53 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:06
2009-10-12 02:54 | 60.008 | 3695.1243 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7911.18 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 623 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:06
2009-10-12 02:54 | 60.008 | 3694.6807 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7911.51 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 623.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:06
2009-10-12 02:54 | 60.005 | 3694.7407 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7911.84 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 624 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:06
2009-10-12 02:54 | 60.005 | 3694.1987 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7912.17 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 624.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:06
2009-10-12 02:54 | 60.003 | 3693.7495 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7912.5 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 625 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:06
2009-10-12 02:54 | 59.999 | 3693.624 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7912.83 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 625.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:06
2009-10-12 02:54 | 59.997 | 3692.8062 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7913.16 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 626 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:06
2009-10-12 02:54 | 59.999 | 3691.1499 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7913.49 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 626.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:06
2009-10-12 02:54 | 60 | 3691.4067 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7913.82 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 627 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:07
2009-10-12 02:54 | 59.998 | 3691.0769 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7914.15 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 627.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:48 | 2009-10-12 04:07
2009-10-12 02:54 | 59.995 | 3690.5876 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7914.48 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 628 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:49 | 2009-10-12 04:07
2009-10-12 02:54 | 59.994 | 3689.7974 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7914.81 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 628.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:49 | 2009-10-12 04:07
2009-10-12 02:54 | 59.992 | 3688.4827 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7915.14 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 629 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:30 | 2009-10-12 03:49 | 2009-10-12 04:07
2009-10-12 02:54 | 59.993 | 3689.4453 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7915.47 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 629.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:31 | 2009-10-12 03:49 | 2009-10-12 04:07
2009-10-12 02:54 | 59.988 | 3689.5535 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7915.8 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 630 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:31 | 2009-10-12 03:49 | 2009-10-12 04:07
2009-10-12 02:54 | 59.985 | 3689.5249 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7916.13 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 630.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:31 | 2009-10-12 03:49 | 2009-10-12 04:07
2009-10-12 02:54 | 59.986 | 3689.7356 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7916.46 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 631 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:31 | 2009-10-12 03:49 | 2009-10-12 04:07
2009-10-12 02:54 | 59.988 | 3688.8528 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7916.79 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 631.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:31 | 2009-10-12 03:49 | 2009-10-12 04:07
2009-10-12 02:54 | 59.988 | 3688.2402 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7917.12 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 632 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:12 | 2009-10-12 03:31 | 2009-10-12 03:49 | 2009-10-12 04:08
2009-10-12 02:54 | 59.985 | 3687.4937 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7917.45 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 632.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:13 | 2009-10-12 03:31 | 2009-10-12 03:49 | 2009-10-12 04:08
2009-10-12 02:54 | 59.983 | 3687.4753 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7917.78 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 633 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:13 | 2009-10-12 03:31 | 2009-10-12 03:49 | 2009-10-12 04:08
2009-10-12 02:54 | 59.983 | 3686.7073 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7918.11 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 633.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:13 | 2009-10-12 03:31 | 2009-10-12 03:49 | 2009-10-12 04:08
2009-10-12 02:54 | 59.985 | 3685.6597 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7918.44 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 634 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:13 | 2009-10-12 03:31 | 2009-10-12 03:50 | 2009-10-12 04:08
2009-10-12 02:54 | 59.986 | 3684.5098 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7918.77 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 634.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:13 | 2009-10-12 03:31 | 2009-10-12 03:50 | 2009-10-12 04:08
2009-10-12 02:54 | 59.987 | 3684.3335 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7919.1 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 635 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:13 | 2009-10-12 03:31 | 2009-10-12 03:50 | 2009-10-12 04:08
2009-10-12 02:54 | 59.99 | 3683.9109 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7919.43 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 635.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:13 | 2009-10-12 03:31 | 2009-10-12 03:50 | 2009-10-12 04:08
2009-10-12 02:54 | 59.986 | 3683.7349 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7919.76 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 636 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:13 | 2009-10-12 03:31 | 2009-10-12 03:50 | 2009-10-12 04:08
2009-10-12 02:54 | 59.985 | 3684.2083 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7920.09 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 636.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:13 | 2009-10-12 03:31 | 2009-10-12 03:50 | 2009-10-12 04:08
2009-10-12 02:54 | 59.984 | 3683.811 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7920.42 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 637 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:13 | 2009-10-12 03:32 | 2009-10-12 03:50 | 2009-10-12 04:09
2009-10-12 02:54 | 59.983 | 3683.4731 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7920.75 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 637.5 | 10 | 0 | 2009-10-12 02:54 | 2009-10-12 03:13 | 2009-10-12 03:32 | 2009-10-12 03:50 | 2009-10-12 04:09
2009-10-12 02:55 | 59.982 | 3684.2578 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7921.08 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 638 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:13 | 2009-10-12 03:32 | 2009-10-12 03:50 | 2009-10-12 04:09
2009-10-12 02:55 | 59.982 | 3684.8843 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7921.41 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 638.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:13 | 2009-10-12 03:32 | 2009-10-12 03:50 | 2009-10-12 04:09
2009-10-12 02:55 | 59.98 | 3685.0918 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7921.74 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 639 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:13 | 2009-10-12 03:32 | 2009-10-12 03:50 | 2009-10-12 04:09
2009-10-12 02:55 | 59.978 | 3685.6543 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7922.07 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 639.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:13 | 2009-10-12 03:32 | 2009-10-12 03:50 | 2009-10-12 04:09
2009-10-12 02:55 | 59.977 | 3685.0869 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7922.4 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 640 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:13 | 2009-10-12 03:32 | 2009-10-12 03:51 | 2009-10-12 04:09
2009-10-12 02:55 | 59.975 | 3685.4912 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7922.73 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 640.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:13 | 2009-10-12 03:32 | 2009-10-12 03:51 | 2009-10-12 04:09
2009-10-12 02:55 | 59.973 | 3685.196 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7923.06 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 641 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:13 | 2009-10-12 03:32 | 2009-10-12 03:51 | 2009-10-12 04:09
2009-10-12 02:55 | 59.975 | 3687.4124 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7923.39 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 641.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:13 | 2009-10-12 03:32 | 2009-10-12 03:51 | 2009-10-12 04:09
2009-10-12 02:55 | 59.976 | 3688.417 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7923.72 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 642 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:13 | 2009-10-12 03:32 | 2009-10-12 03:51 | 2009-10-12 04:10
2009-10-12 02:55 | 59.976 | 3688.5986 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7924.05 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 642.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:32 | 2009-10-12 03:51 | 2009-10-12 04:10
2009-10-12 02:55 | 59.979 | 3687.8477 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7924.38 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 643 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:32 | 2009-10-12 03:51 | 2009-10-12 04:10
2009-10-12 02:55 | 59.982 | 3686.6782 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7924.71 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 643.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:32 | 2009-10-12 03:51 | 2009-10-12 04:10
2009-10-12 02:55 | 59.979 | 3685.7822 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7925.04 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 644 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:32 | 2009-10-12 03:51 | 2009-10-12 04:10
2009-10-12 02:55 | 59.979 | 3684.8901 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7925.37 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 644.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:51 | 2009-10-12 04:10
2009-10-12 02:55 | 59.977 | 3685.1426 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7925.7 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 645 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:51 | 2009-10-12 04:10
2009-10-12 02:55 | 59.977 | 3684.5493 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7926.03 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 645.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:51 | 2009-10-12 04:10
2009-10-12 02:55 | 59.978 | 3684.0933 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7926.36 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 646 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:10
2009-10-12 02:55 | 59.978 | 3684.5547 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7926.69 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 646.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:10
2009-10-12 02:55 | 59.978 | 3682.8142 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7927.02 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 647 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:11
2009-10-12 02:55 | 59.979 | 3682.3176 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7927.35 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 647.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:11
2009-10-12 02:55 | 59.983 | 3682.3657 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7927.68 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 648 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:11
2009-10-12 02:55 | 59.981 | 3682.6475 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7928.01 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 648.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:11
2009-10-12 02:55 | 59.98 | 3682.8555 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7928.34 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 649 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:11
2009-10-12 02:55 | 59.978 | 3683.5566 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7928.67 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 649.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:11
2009-10-12 02:55 | 59.979 | 3684.0518 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7929 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 650 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:11
2009-10-12 02:55 | 59.978 | 3684.3184 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7929.33 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 650.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:11
2009-10-12 02:55 | 59.979 | 3686.0488 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7929.66 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 651 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:11
2009-10-12 02:55 | 59.983 | 3686.6294 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7929.99 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 651.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:33 | 2009-10-12 03:52 | 2009-10-12 04:11
2009-10-12 02:55 | 59.987 | 3685.2864 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7930.32 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 652 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:14 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:12
2009-10-12 02:55 | 59.99 | 3683.4146 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7930.65 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 652.5 | 10 | 0 | 2009-10-12 02:55 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:12
2009-10-12 02:56 | 59.992 | 3682.416 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7930.98 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 653 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:12
2009-10-12 02:56 | 59.993 | 3681.4026 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7931.31 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 653.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:12
2009-10-12 02:56 | 59.99 | 3679.0125 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7931.64 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 654 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:12
2009-10-12 02:56 | 59.988 | 3679.4358 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7931.97 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 654.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:12
2009-10-12 02:56 | 59.988 | 3671.7612 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7932.3 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 655 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:12
2009-10-12 02:56 | 59.99 | 3670.7168 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7932.63 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 655.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:12
2009-10-12 02:56 | 59.993 | 3670.1594 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7932.96 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 656 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:12
2009-10-12 02:56 | 59.994 | 3679.0005 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7933.29 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 656.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:12
2009-10-12 02:56 | 59.993 | 3680.1763 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7933.62 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 657 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:13
2009-10-12 02:56 | 59.994 | 3681.7988 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7933.95 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 657.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:53 | 2009-10-12 04:13
2009-10-12 02:56 | 59.994 | 3682.7004 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7934.28 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 658 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:54 | 2009-10-12 04:13
2009-10-12 02:56 | 59.993 | 3684.1157 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7934.61 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 658.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:54 | 2009-10-12 04:13
2009-10-12 02:56 | 59.989 | 3685.0303 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7934.94 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 659 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:34 | 2009-10-12 03:54 | 2009-10-12 04:13
2009-10-12 02:56 | 59.984 | 3684.8784 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7935.27 | 1 | 0 | 1 | -0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 659.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:35 | 2009-10-12 03:54 | 2009-10-12 04:13
2009-10-12 02:56 | 59.986 | 3684.165 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7935.6 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 660 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:35 | 2009-10-12 03:54 | 2009-10-12 04:13
2009-10-12 02:56 | 59.985 | 3684.478 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7935.93 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 660.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:35 | 2009-10-12 03:54 | 2009-10-12 04:13
2009-10-12 02:56 | 59.988 | 3685.5837 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7936.26 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 661 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:35 | 2009-10-12 03:54 | 2009-10-12 04:13
2009-10-12 02:56 | 59.987 | 3685.1484 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7936.59 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 661.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:35 | 2009-10-12 03:54 | 2009-10-12 04:13
2009-10-12 02:56 | 59.986 | 3684.5867 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7936.92 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 662 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:15 | 2009-10-12 03:35 | 2009-10-12 03:54 | 2009-10-12 04:14
2009-10-12 02:56 | 59.987 | 3684.9761 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7937.25 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 662.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:16 | 2009-10-12 03:35 | 2009-10-12 03:54 | 2009-10-12 04:14
2009-10-12 02:56 | 59.985 | 3683.6743 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7937.58 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 663 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:16 | 2009-10-12 03:35 | 2009-10-12 03:54 | 2009-10-12 04:14
2009-10-12 02:56 | 59.982 | 3684.8721 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7937.91 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 663.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:16 | 2009-10-12 03:35 | 2009-10-12 03:54 | 2009-10-12 04:14
2009-10-12 02:56 | 59.981 | 3684.2446 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7938.24 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 664 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:16 | 2009-10-12 03:35 | 2009-10-12 03:55 | 2009-10-12 04:14
2009-10-12 02:56 | 59.982 | 3684.7114 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7938.57 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 664.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:16 | 2009-10-12 03:35 | 2009-10-12 03:55 | 2009-10-12 04:14
2009-10-12 02:56 | 59.987 | 3685.5891 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7938.9 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 665 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:16 | 2009-10-12 03:35 | 2009-10-12 03:55 | 2009-10-12 04:14
2009-10-12 02:56 | 59.992 | 3683.7358 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7939.23 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 665.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:16 | 2009-10-12 03:35 | 2009-10-12 03:55 | 2009-10-12 04:14
2009-10-12 02:56 | 59.997 | 3682.5789 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7939.56 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 666 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:16 | 2009-10-12 03:35 | 2009-10-12 03:55 | 2009-10-12 04:14
2009-10-12 02:56 | 60 | 3682.2341 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7939.89 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 666.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:16 | 2009-10-12 03:35 | 2009-10-12 03:55 | 2009-10-12 04:14
2009-10-12 02:56 | 60.003 | 3682.1377 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7940.22 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 667 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:16 | 2009-10-12 03:36 | 2009-10-12 03:55 | 2009-10-12 04:15
2009-10-12 02:56 | 60.003 | 3682.2239 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7940.55 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 667.5 | 10 | 0 | 2009-10-12 02:56 | 2009-10-12 03:16 | 2009-10-12 03:36 | 2009-10-12 03:55 | 2009-10-12 04:15
2009-10-12 02:57 | 60.003 | 3681.689 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7940.88 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 668 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:16 | 2009-10-12 03:36 | 2009-10-12 03:55 | 2009-10-12 04:15
2009-10-12 02:57 | 60.002 | 3681.4585 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7941.21 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 668.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:16 | 2009-10-12 03:36 | 2009-10-12 03:55 | 2009-10-12 04:15
2009-10-12 02:57 | 60.003 | 3681.6504 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7941.54 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 669 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:16 | 2009-10-12 03:36 | 2009-10-12 03:55 | 2009-10-12 04:15
2009-10-12 02:57 | 60.002 | 3681.0129 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7941.87 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 669.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:16 | 2009-10-12 03:36 | 2009-10-12 03:55 | 2009-10-12 04:15
2009-10-12 02:57 | 60.003 | 3680.167 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7942.2 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 670 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:16 | 2009-10-12 03:36 | 2009-10-12 03:56 | 2009-10-12 04:15
2009-10-12 02:57 | 60.004 | 3679.9429 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7942.53 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 670.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:16 | 2009-10-12 03:36 | 2009-10-12 03:56 | 2009-10-12 04:15
2009-10-12 02:57 | 60.005 | 3679.4292 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7942.86 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 671 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:16 | 2009-10-12 03:36 | 2009-10-12 03:56 | 2009-10-12 04:15
2009-10-12 02:57 | 60.006 | 3679.6692 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7943.19 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 671.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:16 | 2009-10-12 03:36 | 2009-10-12 03:56 | 2009-10-12 04:15
2009-10-12 02:57 | 60.009 | 3678.9812 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7943.52 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 672 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:16 | 2009-10-12 03:36 | 2009-10-12 03:56 | 2009-10-12 04:16
2009-10-12 02:57 | 60.012 | 3678.2673 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7943.85 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 672.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:36 | 2009-10-12 03:56 | 2009-10-12 04:16
2009-10-12 02:57 | 60.017 | 3676.7961 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7944.18 | 1 | 1 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 673 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:36 | 2009-10-12 03:56 | 2009-10-12 04:16
2009-10-12 02:57 | 60.021 | 3676.8096 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7944.51 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 673.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:36 | 2009-10-12 03:56 | 2009-10-12 04:16
2009-10-12 02:57 | 60.022 | 3674.7976 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7944.84 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 674 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:36 | 2009-10-12 03:56 | 2009-10-12 04:16
2009-10-12 02:57 | 60.021 | 3673.906 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7945.17 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 674.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:56 | 2009-10-12 04:16
2009-10-12 02:57 | 60.02 | 3671.145 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7945.5 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 675 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:56 | 2009-10-12 04:16
2009-10-12 02:57 | 60.018 | 3670.5098 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7945.83 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 675.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:56 | 2009-10-12 04:16
2009-10-12 02:57 | 60.021 | 3673.6479 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7946.16 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 676 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:16
2009-10-12 02:57 | 60.02 | 3673.6838 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7946.49 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 676.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:16
2009-10-12 02:57 | 60.02 | 3675.8647 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7946.82 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 677 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:17
2009-10-12 02:57 | 60.018 | 3676.6758 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7947.15 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 677.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:17
2009-10-12 02:57 | 60.018 | 3676.4038 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7947.48 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 678 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:17
2009-10-12 02:57 | 60.019 | 3676.437 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7947.81 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 678.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:17
2009-10-12 02:57 | 60.019 | 3677.1848 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7948.14 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 679 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:17
2009-10-12 02:57 | 60.018 | 3677.6589 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7948.47 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 679.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:17
2009-10-12 02:57 | 60.017 | 3678.8284 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7948.8 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 680 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:17
2009-10-12 02:57 | 60.016 | 3679.2888 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7949.13 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 680.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:17
2009-10-12 02:57 | 60.016 | 3678.9146 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7949.46 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 681 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:17
2009-10-12 02:57 | 60.016 | 3679.2756 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7949.79 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 681.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:37 | 2009-10-12 03:57 | 2009-10-12 04:17
2009-10-12 02:57 | 60.015 | 3678.5986 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7950.12 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 682 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:17 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:18
2009-10-12 02:57 | 60.014 | 3678.3669 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7950.45 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 682.5 | 10 | 0 | 2009-10-12 02:57 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:18
2009-10-12 02:58 | 60.014 | 3678.2505 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7950.78 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 683 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:18
2009-10-12 02:58 | 60.013 | 3678.5894 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7951.11 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 683.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:18
2009-10-12 02:58 | 60.013 | 3677.251 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7951.44 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 684 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:18
2009-10-12 02:58 | 60.015 | 3675.6978 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7951.77 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 684.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:18
2009-10-12 02:58 | 60.017 | 3674.6694 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7952.1 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 685 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:18
2009-10-12 02:58 | 60.016 | 3674.8701 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7952.43 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 685.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:18
2009-10-12 02:58 | 60.019 | 3674.4019 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7952.76 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 686 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:18
2009-10-12 02:58 | 60.021 | 3674.5461 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7953.09 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 686.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:18
2009-10-12 02:58 | 60.021 | 3672.9688 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7953.42 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 687 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:19
2009-10-12 02:58 | 60.02 | 3671.9136 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7953.75 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 687.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:58 | 2009-10-12 04:19
2009-10-12 02:58 | 60.022 | 3671.9819 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7954.08 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 688 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:59 | 2009-10-12 04:19
2009-10-12 02:58 | 60.024 | 3670.9456 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7954.41 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 688.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:59 | 2009-10-12 04:19
2009-10-12 02:58 | 60.026 | 3670.821 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7954.74 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 689 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:38 | 2009-10-12 03:59 | 2009-10-12 04:19
2009-10-12 02:58 | 60.025 | 3671.0596 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7955.07 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 689.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:39 | 2009-10-12 03:59 | 2009-10-12 04:19
2009-10-12 02:58 | 60.026 | 3671.5386 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7955.4 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 690 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:39 | 2009-10-12 03:59 | 2009-10-12 04:19
2009-10-12 02:58 | 60.022 | 3673.7937 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7955.73 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 690.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:39 | 2009-10-12 03:59 | 2009-10-12 04:19
2009-10-12 02:58 | 60.021 | 3674.0095 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7956.06 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 691 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:39 | 2009-10-12 03:59 | 2009-10-12 04:19
2009-10-12 02:58 | 60.022 | 3675.1016 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7956.39 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 691.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:39 | 2009-10-12 03:59 | 2009-10-12 04:19
2009-10-12 02:58 | 60.024 | 3675.2842 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7956.72 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 692 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:18 | 2009-10-12 03:39 | 2009-10-12 03:59 | 2009-10-12 04:20
2009-10-12 02:58 | 60.027 | 3676.0513 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7957.05 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 692.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:19 | 2009-10-12 03:39 | 2009-10-12 03:59 | 2009-10-12 04:20
2009-10-12 02:58 | 60.029 | 3675.7036 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7957.38 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 693 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:19 | 2009-10-12 03:39 | 2009-10-12 03:59 | 2009-10-12 04:20
2009-10-12 02:58 | 60.028 | 3672.5835 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7957.71 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 693.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:19 | 2009-10-12 03:39 | 2009-10-12 03:59 | 2009-10-12 04:20
2009-10-12 02:58 | 60.028 | 3671.3428 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7958.04 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 694 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:19 | 2009-10-12 03:39 | 2009-10-12 04:00 | 2009-10-12 04:20
2009-10-12 02:58 | 60.032 | 3670.2317 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7958.37 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 694.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:19 | 2009-10-12 03:39 | 2009-10-12 04:00 | 2009-10-12 04:20
2009-10-12 02:58 | 60.035 | 3668.6538 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7958.7 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 695 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:19 | 2009-10-12 03:39 | 2009-10-12 04:00 | 2009-10-12 04:20
2009-10-12 02:58 | 60.03 | 3668.7671 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7959.03 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 695.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:19 | 2009-10-12 03:39 | 2009-10-12 04:00 | 2009-10-12 04:20
2009-10-12 02:58 | 60.028 | 3666.3123 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7959.36 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 696 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:19 | 2009-10-12 03:39 | 2009-10-12 04:00 | 2009-10-12 04:20
2009-10-12 02:58 | 60.021 | 3667.3218 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7959.69 | 1 | 1 | 1 | -0.007 | 0.007 |  | 350 | -223.0157 | 16 | 696.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:19 | 2009-10-12 03:39 | 2009-10-12 04:00 | 2009-10-12 04:20
2009-10-12 02:58 | 60.021 | 3657.1641 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7960.02 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 697 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:19 | 2009-10-12 03:40 | 2009-10-12 04:00 | 2009-10-12 04:21
2009-10-12 02:58 | 60.024 | 3657.7141 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7960.35 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 697.5 | 10 | 0 | 2009-10-12 02:58 | 2009-10-12 03:19 | 2009-10-12 03:40 | 2009-10-12 04:00 | 2009-10-12 04:21
2009-10-12 02:59 | 60.025 | 3668.6375 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7960.68 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 698 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:19 | 2009-10-12 03:40 | 2009-10-12 04:00 | 2009-10-12 04:21
2009-10-12 02:59 | 60.024 | 3669.3088 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7961.01 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 698.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:19 | 2009-10-12 03:40 | 2009-10-12 04:00 | 2009-10-12 04:21
2009-10-12 02:59 | 60.022 | 3670.1123 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7961.34 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 699 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:19 | 2009-10-12 03:40 | 2009-10-12 04:00 | 2009-10-12 04:21
2009-10-12 02:59 | 60.023 | 3670.7354 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7961.67 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 699.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:19 | 2009-10-12 03:40 | 2009-10-12 04:00 | 2009-10-12 04:21
2009-10-12 02:59 | 60.021 | 3671.332 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7962 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 700 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:19 | 2009-10-12 03:40 | 2009-10-12 04:01 | 2009-10-12 04:21
2009-10-12 02:59 | 60.02 | 3672.0955 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7962.33 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 700.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:19 | 2009-10-12 03:40 | 2009-10-12 04:01 | 2009-10-12 04:21
2009-10-12 02:59 | 60.02 | 3672.6831 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7962.66 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 701 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:19 | 2009-10-12 03:40 | 2009-10-12 04:01 | 2009-10-12 04:21
2009-10-12 02:59 | 60.02 | 3673.8325 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7962.99 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 701.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:19 | 2009-10-12 03:40 | 2009-10-12 04:01 | 2009-10-12 04:21
2009-10-12 02:59 | 60.02 | 3674.6448 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7963.32 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 702 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:19 | 2009-10-12 03:40 | 2009-10-12 04:01 | 2009-10-12 04:22
2009-10-12 02:59 | 60.017 | 3675.6406 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7963.65 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 702.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:40 | 2009-10-12 04:01 | 2009-10-12 04:22
2009-10-12 02:59 | 60.014 | 3675.9707 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7963.98 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 703 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:40 | 2009-10-12 04:01 | 2009-10-12 04:22
2009-10-12 02:59 | 60.012 | 3677.0093 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7964.31 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 703.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:40 | 2009-10-12 04:01 | 2009-10-12 04:22
2009-10-12 02:59 | 60.01 | 3678.3137 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7964.64 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 704 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:40 | 2009-10-12 04:01 | 2009-10-12 04:22
2009-10-12 02:59 | 60.011 | 3679.3928 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7964.97 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 704.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:01 | 2009-10-12 04:22
2009-10-12 02:59 | 60.01 | 3680.0203 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7965.3 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 705 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:01 | 2009-10-12 04:22
2009-10-12 02:59 | 60.01 | 3679.7915 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7965.63 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 705.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:01 | 2009-10-12 04:22
2009-10-12 02:59 | 60.01 | 3679.5967 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7965.96 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 706 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:22
2009-10-12 02:59 | 60.012 | 3680.3149 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7966.29 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 706.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:22
2009-10-12 02:59 | 60.012 | 3680.1104 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7966.62 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 707 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:23
2009-10-12 02:59 | 60.013 | 3679.0615 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7966.95 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 707.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:23
2009-10-12 02:59 | 60.014 | 3679.1272 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7967.28 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 708 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:23
2009-10-12 02:59 | 60.013 | 3679.5869 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7967.61 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 708.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:23
2009-10-12 02:59 | 60.012 | 3679.6367 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7967.94 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 709 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:23
2009-10-12 02:59 | 60.011 | 3679.02 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7968.27 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 709.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:23
2009-10-12 02:59 | 60.01 | 3678.4177 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7968.6 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 710 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:23
2009-10-12 02:59 | 60.008 | 3679.3831 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7968.93 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 710.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:23
2009-10-12 02:59 | 60.01 | 3679.6809 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7969.26 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 711 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:23
2009-10-12 02:59 | 60.011 | 3679.9324 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7969.59 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 711.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:41 | 2009-10-12 04:02 | 2009-10-12 04:23
2009-10-12 02:59 | 60.013 | 3679.1382 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7969.92 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 712 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:20 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:24
2009-10-12 02:59 | 60.016 | 3678.4688 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7970.25 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 712.5 | 10 | 0 | 2009-10-12 02:59 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:24
2009-10-12 03:00 | 60.018 | 3678.4985 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7970.58 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 713 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:24
2009-10-12 03:00 | 60.019 | 3678.4556 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7970.91 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 713.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:24
2009-10-12 03:00 | 60.019 | 3677.6152 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7971.24 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 714 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:24
2009-10-12 03:00 | 60.019 | 3677.4463 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7971.57 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 714.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:24
2009-10-12 03:00 | 60.02 | 3677.4314 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7971.9 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 715 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:24
2009-10-12 03:00 | 60.02 | 3677.4509 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7972.23 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 715.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:24
2009-10-12 03:00 | 60.018 | 3677.3154 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7972.56 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 716 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:24
2009-10-12 03:00 | 60.018 | 3678.1511 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7972.89 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 716.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:24
2009-10-12 03:00 | 60.016 | 3678.3621 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7973.22 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 717 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:25
2009-10-12 03:00 | 60.016 | 3678.8735 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7973.55 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 717.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:03 | 2009-10-12 04:25
2009-10-12 03:00 | 60.019 | 3680.7708 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7973.88 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 718 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:04 | 2009-10-12 04:25
2009-10-12 03:00 | 60.023 | 3681.0581 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7974.21 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 718.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:04 | 2009-10-12 04:25
2009-10-12 03:00 | 60.022 | 3680.353 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7974.54 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 719 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:42 | 2009-10-12 04:04 | 2009-10-12 04:25
2009-10-12 03:00 | 60.018 | 3679.1665 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7974.87 | 1 | 1 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 719.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:43 | 2009-10-12 04:04 | 2009-10-12 04:25
2009-10-12 03:00 | 60.015 | 3679.5532 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7975.2 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 720 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:43 | 2009-10-12 04:04 | 2009-10-12 04:25
2009-10-12 03:00 | 60.016 | 3680.6724 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7975.53 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 720.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:43 | 2009-10-12 04:04 | 2009-10-12 04:25
2009-10-12 03:00 | 60.017 | 3682.7297 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7975.86 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 721 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:43 | 2009-10-12 04:04 | 2009-10-12 04:25
2009-10-12 03:00 | 60.015 | 3682.7136 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7976.19 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 721.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:43 | 2009-10-12 04:04 | 2009-10-12 04:25
2009-10-12 03:00 | 60.01 | 3681.9146 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7976.52 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 722 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:21 | 2009-10-12 03:43 | 2009-10-12 04:04 | 2009-10-12 04:26
2009-10-12 03:00 | 60.004 | 3682.0103 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7976.85 | 1 | 1 | 1 | -0.0059967 | 0.0059967 |  | 350 | -223.0157 | 16 | 722.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:22 | 2009-10-12 03:43 | 2009-10-12 04:04 | 2009-10-12 04:26
2009-10-12 03:00 | 59.999 | 3682.4834 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7977.18 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 723 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:22 | 2009-10-12 03:43 | 2009-10-12 04:04 | 2009-10-12 04:26
2009-10-12 03:00 | 59.995 | 3683.8135 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7977.51 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 723.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:22 | 2009-10-12 03:43 | 2009-10-12 04:04 | 2009-10-12 04:26
2009-10-12 03:00 | 59.99 | 3685.3064 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7977.84 | 1 | 0 | 1 | -0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 724 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:22 | 2009-10-12 03:43 | 2009-10-12 04:05 | 2009-10-12 04:26
2009-10-12 03:00 | 59.982 | 3684.8457 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7978.17 | 1 | 0 | 1 | -0.0080032 | 0.0080032 |  | 350 | -223.0157 | 16 | 724.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:22 | 2009-10-12 03:43 | 2009-10-12 04:05 | 2009-10-12 04:26
2009-10-12 03:00 | 59.974 | 3684.6426 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7978.5 | 1 | 0 | 1 | -0.0079994 | 0.0079994 |  | 350 | -223.0157 | 16 | 725 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:22 | 2009-10-12 03:43 | 2009-10-12 04:05 | 2009-10-12 04:26
2009-10-12 03:00 | 59.97 | 3687.5271 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7978.83 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 725.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:22 | 2009-10-12 03:43 | 2009-10-12 04:05 | 2009-10-12 04:26
2009-10-12 03:00 | 59.97 | 3689.4038 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7979.16 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 726 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:22 | 2009-10-12 03:43 | 2009-10-12 04:05 | 2009-10-12 04:26
2009-10-12 03:00 | 59.968 | 3692.2874 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7979.49 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 726.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:22 | 2009-10-12 03:43 | 2009-10-12 04:05 | 2009-10-12 04:26
2009-10-12 03:00 | 59.968 | 3692.9663 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7979.82 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 727 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:22 | 2009-10-12 03:44 | 2009-10-12 04:05 | 2009-10-12 04:27
2009-10-12 03:00 | 59.968 | 3693.7932 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7980.15 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 727.5 | 10 | 0 | 2009-10-12 03:00 | 2009-10-12 03:22 | 2009-10-12 03:44 | 2009-10-12 04:05 | 2009-10-12 04:27
2009-10-12 03:01 | 59.972 | 3694.3972 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7980.48 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 728 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:22 | 2009-10-12 03:44 | 2009-10-12 04:05 | 2009-10-12 04:27
2009-10-12 03:01 | 59.967 | 3694.9736 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7980.81 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 728.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:22 | 2009-10-12 03:44 | 2009-10-12 04:05 | 2009-10-12 04:27
2009-10-12 03:01 | 59.966 | 3697.407 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7981.14 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 729 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:22 | 2009-10-12 03:44 | 2009-10-12 04:05 | 2009-10-12 04:27
2009-10-12 03:01 | 59.964 | 3698.502 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7981.47 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 729.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:22 | 2009-10-12 03:44 | 2009-10-12 04:05 | 2009-10-12 04:27
2009-10-12 03:01 | 59.965 | 3698.6169 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7981.8 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 730 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:22 | 2009-10-12 03:44 | 2009-10-12 04:06 | 2009-10-12 04:27
2009-10-12 03:01 | 59.966 | 3698.9924 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7982.13 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 730.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:22 | 2009-10-12 03:44 | 2009-10-12 04:06 | 2009-10-12 04:27
2009-10-12 03:01 | 59.963 | 3699.8501 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7982.46 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 731 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:22 | 2009-10-12 03:44 | 2009-10-12 04:06 | 2009-10-12 04:27
2009-10-12 03:01 | 59.963 | 3702.6448 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7982.79 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 731.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:22 | 2009-10-12 03:44 | 2009-10-12 04:06 | 2009-10-12 04:27
2009-10-12 03:01 | 59.965 | 3701.9885 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7983.12 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 732 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:22 | 2009-10-12 03:44 | 2009-10-12 04:06 | 2009-10-12 04:28
2009-10-12 03:01 | 59.968 | 3702.218 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7983.45 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 732.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:44 | 2009-10-12 04:06 | 2009-10-12 04:28
2009-10-12 03:01 | 59.97 | 3704.0234 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7983.78 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 733 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:44 | 2009-10-12 04:06 | 2009-10-12 04:28
2009-10-12 03:01 | 59.97 | 3703.3655 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7984.11 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 733.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:44 | 2009-10-12 04:06 | 2009-10-12 04:28
2009-10-12 03:01 | 59.97 | 3702.9883 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7984.44 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 734 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:44 | 2009-10-12 04:06 | 2009-10-12 04:28
2009-10-12 03:01 | 59.973 | 3703.8137 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7984.77 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 734.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:06 | 2009-10-12 04:28
2009-10-12 03:01 | 59.972 | 3704.8994 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7985.1 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 735 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:06 | 2009-10-12 04:28
2009-10-12 03:01 | 59.976 | 3705.625 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7985.43 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 735.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:06 | 2009-10-12 04:28
2009-10-12 03:01 | 59.975 | 3704.2935 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7985.76 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 736 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:28
2009-10-12 03:01 | 59.975 | 3702.0942 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7986.09 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 736.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:28
2009-10-12 03:01 | 59.977 | 3701.9438 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7986.42 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 737 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:29
2009-10-12 03:01 | 59.976 | 3703.1421 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7986.75 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 737.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:29
2009-10-12 03:01 | 59.976 | 3704.6689 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7987.08 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 738 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:29
2009-10-12 03:01 | 59.974 | 3705.3757 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7987.41 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 738.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:29
2009-10-12 03:01 | 59.975 | 3705.6624 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7987.74 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 739 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:29
2009-10-12 03:01 | 59.974 | 3705.8547 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7988.07 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 739.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:29
2009-10-12 03:01 | 59.974 | 3706.7764 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7988.4 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 740 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:29
2009-10-12 03:01 | 59.976 | 3707.5139 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7988.73 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 740.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:29
2009-10-12 03:01 | 59.977 | 3706.9282 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7989.06 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 741 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:29
2009-10-12 03:01 | 59.979 | 3706.446 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7989.39 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 741.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:45 | 2009-10-12 04:07 | 2009-10-12 04:29
2009-10-12 03:01 | 59.981 | 3706.335 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7989.72 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 742 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:23 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:30
2009-10-12 03:01 | 59.983 | 3706.771 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7990.05 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 742.5 | 10 | 0 | 2009-10-12 03:01 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:30
2009-10-12 03:02 | 59.985 | 3705.9431 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7990.38 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 743 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:30
2009-10-12 03:02 | 59.983 | 3704.1272 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7990.71 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 743.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:30
2009-10-12 03:02 | 59.98 | 3704.7773 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7991.04 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 744 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:30
2009-10-12 03:02 | 59.979 | 3705.9744 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7991.37 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 744.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:30
2009-10-12 03:02 | 59.983 | 3705.9675 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7991.7 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 745 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:30
2009-10-12 03:02 | 59.987 | 3705.3564 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7992.03 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 745.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:30
2009-10-12 03:02 | 59.986 | 3704.6831 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7992.36 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 746 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:30
2009-10-12 03:02 | 59.984 | 3703.9133 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7992.69 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 746.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:30
2009-10-12 03:02 | 59.98 | 3704.3606 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7993.02 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 747 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:31
2009-10-12 03:02 | 59.982 | 3704.9883 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7993.35 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 747.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:08 | 2009-10-12 04:31
2009-10-12 03:02 | 59.984 | 3705.0498 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7993.68 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 748 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:09 | 2009-10-12 04:31
2009-10-12 03:02 | 59.985 | 3704.8928 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7994.01 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 748.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:09 | 2009-10-12 04:31
2009-10-12 03:02 | 59.987 | 3703.7407 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7994.34 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 749 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:46 | 2009-10-12 04:09 | 2009-10-12 04:31
2009-10-12 03:02 | 59.989 | 3701.8311 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7994.67 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 749.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:47 | 2009-10-12 04:09 | 2009-10-12 04:31
2009-10-12 03:02 | 59.992 | 3701.7952 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7995 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 750 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:47 | 2009-10-12 04:09 | 2009-10-12 04:31
2009-10-12 03:02 | 59.996 | 3700.0698 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7995.33 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 750.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:47 | 2009-10-12 04:09 | 2009-10-12 04:31
2009-10-12 03:02 | 59.999 | 3701.3081 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7995.66 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 751 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:47 | 2009-10-12 04:09 | 2009-10-12 04:31
2009-10-12 03:02 | 59.997 | 3700.4294 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7995.99 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 751.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:47 | 2009-10-12 04:09 | 2009-10-12 04:31
2009-10-12 03:02 | 59.997 | 3700.9128 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7996.32 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 752 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:24 | 2009-10-12 03:47 | 2009-10-12 04:09 | 2009-10-12 04:32
2009-10-12 03:02 | 59.997 | 3700.541 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7996.65 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 752.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:25 | 2009-10-12 03:47 | 2009-10-12 04:09 | 2009-10-12 04:32
2009-10-12 03:02 | 59.997 | 3699.9265 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7996.98 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 753 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:25 | 2009-10-12 03:47 | 2009-10-12 04:09 | 2009-10-12 04:32
2009-10-12 03:02 | 59.996 | 3700.8582 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7997.31 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 753.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:25 | 2009-10-12 03:47 | 2009-10-12 04:09 | 2009-10-12 04:32
2009-10-12 03:02 | 59.997 | 3700.5486 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7997.64 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 754 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:25 | 2009-10-12 03:47 | 2009-10-12 04:10 | 2009-10-12 04:32
2009-10-12 03:02 | 59.996 | 3700.6135 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7997.97 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 754.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:25 | 2009-10-12 03:47 | 2009-10-12 04:10 | 2009-10-12 04:32
2009-10-12 03:02 | 59.998 | 3700.2239 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7998.3 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 755 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:25 | 2009-10-12 03:47 | 2009-10-12 04:10 | 2009-10-12 04:32
2009-10-12 03:02 | 60.003 | 3699.5 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7998.63 | 1 | 1 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 755.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:25 | 2009-10-12 03:47 | 2009-10-12 04:10 | 2009-10-12 04:32
2009-10-12 03:02 | 60.009 | 3698.0317 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7998.96 | 1 | 1 | 1 | 0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 756 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:25 | 2009-10-12 03:47 | 2009-10-12 04:10 | 2009-10-12 04:32
2009-10-12 03:02 | 60.01 | 3697.96 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7999.29 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 756.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:25 | 2009-10-12 03:47 | 2009-10-12 04:10 | 2009-10-12 04:32
2009-10-12 03:02 | 60.008 | 3699.4087 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7999.62 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 757 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:25 | 2009-10-12 03:48 | 2009-10-12 04:10 | 2009-10-12 04:33
2009-10-12 03:02 | 60.005 | 3699.2407 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7999.95 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 757.5 | 10 | 0 | 2009-10-12 03:02 | 2009-10-12 03:25 | 2009-10-12 03:48 | 2009-10-12 04:10 | 2009-10-12 04:33
2009-10-12 03:03 | 60.004 | 3700.7383 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8000.28 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 758 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:25 | 2009-10-12 03:48 | 2009-10-12 04:10 | 2009-10-12 04:33
2009-10-12 03:03 | 60.006 | 3701.1099 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8000.61 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 758.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:25 | 2009-10-12 03:48 | 2009-10-12 04:10 | 2009-10-12 04:33
2009-10-12 03:03 | 60.003 | 3701.2378 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8000.94 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 759 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:25 | 2009-10-12 03:48 | 2009-10-12 04:10 | 2009-10-12 04:33
2009-10-12 03:03 | 60.001 | 3699.9976 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8001.27 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 759.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:25 | 2009-10-12 03:48 | 2009-10-12 04:10 | 2009-10-12 04:33
2009-10-12 03:03 | 60.002 | 3700.2202 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8001.6 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 760 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:25 | 2009-10-12 03:48 | 2009-10-12 04:11 | 2009-10-12 04:33
2009-10-12 03:03 | 60.004 | 3701.8228 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8001.93 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 760.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:25 | 2009-10-12 03:48 | 2009-10-12 04:11 | 2009-10-12 04:33
2009-10-12 03:03 | 60.007 | 3702.5542 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8002.26 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 761 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:25 | 2009-10-12 03:48 | 2009-10-12 04:11 | 2009-10-12 04:33
2009-10-12 03:03 | 60.007 | 3702.2759 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8002.59 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 761.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:25 | 2009-10-12 03:48 | 2009-10-12 04:11 | 2009-10-12 04:33
2009-10-12 03:03 | 60.008 | 3701.0264 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8002.92 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 762 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:25 | 2009-10-12 03:48 | 2009-10-12 04:11 | 2009-10-12 04:34
2009-10-12 03:03 | 60.008 | 3701.9229 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8003.25 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 762.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:48 | 2009-10-12 04:11 | 2009-10-12 04:34
2009-10-12 03:03 | 60.006 | 3702.9431 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8003.58 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 763 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:48 | 2009-10-12 04:11 | 2009-10-12 04:34
2009-10-12 03:03 | 60.006 | 3704.0928 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8003.91 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 763.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:48 | 2009-10-12 04:11 | 2009-10-12 04:34
2009-10-12 03:03 | 60.006 | 3703.9604 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8004.24 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 764 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:48 | 2009-10-12 04:11 | 2009-10-12 04:34
2009-10-12 03:03 | 60.005 | 3703.8193 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8004.57 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 764.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:11 | 2009-10-12 04:34
2009-10-12 03:03 | 60 | 3704.4551 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8004.9 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 765 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:11 | 2009-10-12 04:34
2009-10-12 03:03 | 59.999 | 3704.3457 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8005.23 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 765.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:11 | 2009-10-12 04:34
2009-10-12 03:03 | 60 | 3705.3291 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8005.56 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 766 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:34
2009-10-12 03:03 | 60 | 3704.9302 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8005.89 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 766.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:34
2009-10-12 03:03 | 60.004 | 3704.4048 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8006.22 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 767 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:35
2009-10-12 03:03 | 60.008 | 3703.6753 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8006.55 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 767.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:35
2009-10-12 03:03 | 60.013 | 3702.748 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8006.88 | 1 | 1 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 768 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:35
2009-10-12 03:03 | 60.015 | 3702.6692 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8007.21 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 768.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:35
2009-10-12 03:03 | 60.015 | 3703.0166 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8007.54 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 769 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:35
2009-10-12 03:03 | 60.012 | 3703.4155 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8007.87 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 769.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:35
2009-10-12 03:03 | 60.009 | 3703.2974 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8008.2 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 770 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:35
2009-10-12 03:03 | 60.005 | 3705.1887 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8008.53 | 1 | 1 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 770.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:35
2009-10-12 03:03 | 60.008 | 3705.2791 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8008.86 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 771 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:35
2009-10-12 03:03 | 60.011 | 3704.646 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8009.19 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 771.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:49 | 2009-10-12 04:12 | 2009-10-12 04:35
2009-10-12 03:03 | 60.011 | 3704.0513 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8009.52 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 772 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:26 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:36
2009-10-12 03:03 | 60.013 | 3703.438 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8009.85 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 772.5 | 10 | 0 | 2009-10-12 03:03 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:36
2009-10-12 03:04 | 60.016 | 3704.2551 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8010.18 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 773 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:36
2009-10-12 03:04 | 60.018 | 3703.7075 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8010.51 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 773.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:36
2009-10-12 03:04 | 60.018 | 3703.8303 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8010.84 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 774 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:36
2009-10-12 03:04 | 60.019 | 3704.5239 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8011.17 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 774.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:36
2009-10-12 03:04 | 60.018 | 3704.1392 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8011.5 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 775 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:36
2009-10-12 03:04 | 60.013 | 3704.27 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8011.83 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 775.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:36
2009-10-12 03:04 | 60.011 | 3705.4294 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8012.16 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 776 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:36
2009-10-12 03:04 | 60.009 | 3705.9419 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8012.49 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 776.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:36
2009-10-12 03:04 | 60.009 | 3705.5398 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8012.82 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 777 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:37
2009-10-12 03:04 | 60.008 | 3705.634 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8013.15 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 777.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:13 | 2009-10-12 04:37
2009-10-12 03:04 | 60.009 | 3705.7485 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8013.48 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 778 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:14 | 2009-10-12 04:37
2009-10-12 03:04 | 60.011 | 3707.2673 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8013.81 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 778.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:14 | 2009-10-12 04:37
2009-10-12 03:04 | 60.015 | 3706.9453 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8014.14 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 779 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:50 | 2009-10-12 04:14 | 2009-10-12 04:37
2009-10-12 03:04 | 60.02 | 3706.6299 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8014.47 | 1 | 1 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 779.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:51 | 2009-10-12 04:14 | 2009-10-12 04:37
2009-10-12 03:04 | 60.021 | 3705.6545 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8014.8 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 780 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:51 | 2009-10-12 04:14 | 2009-10-12 04:37
2009-10-12 03:04 | 60.018 | 3703.8948 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8015.13 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 780.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:51 | 2009-10-12 04:14 | 2009-10-12 04:37
2009-10-12 03:04 | 60.017 | 3704.2239 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8015.46 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 781 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:51 | 2009-10-12 04:14 | 2009-10-12 04:37
2009-10-12 03:04 | 60.019 | 3703.887 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8015.79 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 781.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:51 | 2009-10-12 04:14 | 2009-10-12 04:37
2009-10-12 03:04 | 60.019 | 3704.6484 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8016.12 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 782 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:27 | 2009-10-12 03:51 | 2009-10-12 04:14 | 2009-10-12 04:38
2009-10-12 03:04 | 60.021 | 3704.7954 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8016.45 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 782.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:28 | 2009-10-12 03:51 | 2009-10-12 04:14 | 2009-10-12 04:38
2009-10-12 03:04 | 60.022 | 3704.1665 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8016.78 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 783 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:28 | 2009-10-12 03:51 | 2009-10-12 04:14 | 2009-10-12 04:38
2009-10-12 03:04 | 60.025 | 3702.7642 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8017.11 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 783.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:28 | 2009-10-12 03:51 | 2009-10-12 04:14 | 2009-10-12 04:38
2009-10-12 03:04 | 60.027 | 3702.0083 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8017.44 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 784 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:28 | 2009-10-12 03:51 | 2009-10-12 04:15 | 2009-10-12 04:38
2009-10-12 03:04 | 60.03 | 3700.3601 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8017.77 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 784.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:28 | 2009-10-12 03:51 | 2009-10-12 04:15 | 2009-10-12 04:38
2009-10-12 03:04 | 60.027 | 3701.063 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8018.1 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 785 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:28 | 2009-10-12 03:51 | 2009-10-12 04:15 | 2009-10-12 04:38
2009-10-12 03:04 | 60.023 | 3700.3401 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8018.43 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 785.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:28 | 2009-10-12 03:51 | 2009-10-12 04:15 | 2009-10-12 04:38
2009-10-12 03:04 | 60.021 | 3699.3694 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8018.76 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 786 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:28 | 2009-10-12 03:51 | 2009-10-12 04:15 | 2009-10-12 04:38
2009-10-12 03:04 | 60.023 | 3701.5676 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8019.09 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 786.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:28 | 2009-10-12 03:51 | 2009-10-12 04:15 | 2009-10-12 04:38
2009-10-12 03:04 | 60.023 | 3702.9587 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8019.42 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 787 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:28 | 2009-10-12 03:52 | 2009-10-12 04:15 | 2009-10-12 04:39
2009-10-12 03:04 | 60.02 | 3704.2495 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8019.75 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 787.5 | 10 | 0 | 2009-10-12 03:04 | 2009-10-12 03:28 | 2009-10-12 03:52 | 2009-10-12 04:15 | 2009-10-12 04:39
2009-10-12 03:05 | 60.024 | 3703.6211 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8020.08 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 788 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:28 | 2009-10-12 03:52 | 2009-10-12 04:15 | 2009-10-12 04:39
2009-10-12 03:05 | 60.024 | 3703.374 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8020.41 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 788.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:28 | 2009-10-12 03:52 | 2009-10-12 04:15 | 2009-10-12 04:39
2009-10-12 03:05 | 60.022 | 3703.0359 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8020.74 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 789 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:28 | 2009-10-12 03:52 | 2009-10-12 04:15 | 2009-10-12 04:39
2009-10-12 03:05 | 60.022 | 3703.9307 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8021.07 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 789.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:28 | 2009-10-12 03:52 | 2009-10-12 04:15 | 2009-10-12 04:39
2009-10-12 03:05 | 60.024 | 3704.9473 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8021.4 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 790 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:28 | 2009-10-12 03:52 | 2009-10-12 04:16 | 2009-10-12 04:39
2009-10-12 03:05 | 60.025 | 3704.208 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8021.73 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 790.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:28 | 2009-10-12 03:52 | 2009-10-12 04:16 | 2009-10-12 04:39
2009-10-12 03:05 | 60.023 | 3703.5413 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8022.06 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 791 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:28 | 2009-10-12 03:52 | 2009-10-12 04:16 | 2009-10-12 04:39
2009-10-12 03:05 | 60.024 | 3703.1602 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8022.39 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 791.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:28 | 2009-10-12 03:52 | 2009-10-12 04:16 | 2009-10-12 04:39
2009-10-12 03:05 | 60.02 | 3703.3975 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8022.72 | 1 | 1 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 792 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:28 | 2009-10-12 03:52 | 2009-10-12 04:16 | 2009-10-12 04:40
2009-10-12 03:05 | 60.018 | 3704.3765 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8023.05 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 792.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:52 | 2009-10-12 04:16 | 2009-10-12 04:40
2009-10-12 03:05 | 60.013 | 3705.4412 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8023.38 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 793 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:52 | 2009-10-12 04:16 | 2009-10-12 04:40
2009-10-12 03:05 | 60.008 | 3706.9949 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8023.71 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 | 793.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:52 | 2009-10-12 04:16 | 2009-10-12 04:40
2009-10-12 03:05 | 60.012 | 3710.072 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8024.04 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 794 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:52 | 2009-10-12 04:16 | 2009-10-12 04:40
2009-10-12 03:05 | 60.017 | 3707.9707 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8024.37 | 1 | 1 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 | 794.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:16 | 2009-10-12 04:40
2009-10-12 03:05 | 60.019 | 3707.7671 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8024.7 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 795 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:16 | 2009-10-12 04:40
2009-10-12 03:05 | 60.019 | 3707.6094 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8025.03 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 795.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:16 | 2009-10-12 04:40
2009-10-12 03:05 | 60.015 | 3708.8311 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8025.36 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 796 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:40
2009-10-12 03:05 | 60.016 | 3709.4646 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8025.69 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 796.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:40
2009-10-12 03:05 | 60.015 | 3709.8135 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8026.02 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 797 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:41
2009-10-12 03:05 | 60.016 | 3709.8169 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8026.35 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 797.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:41
2009-10-12 03:05 | 60.014 | 3709.9905 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8026.68 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 798 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:41
2009-10-12 03:05 | 60.016 | 3709.0938 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8027.01 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 798.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:41
2009-10-12 03:05 | 60.018 | 3709.6416 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8027.34 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 799 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:41
2009-10-12 03:05 | 60.019 | 3709.8115 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8027.67 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 799.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:41
2009-10-12 03:05 | 60.016 | 3709.9331 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8028 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 800 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:41
2009-10-12 03:05 | 60.014 | 3710.6768 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8028.33 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 800.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:41
2009-10-12 03:05 | 60.014 | 3710.5911 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8028.66 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 801 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:41
2009-10-12 03:05 | 60.018 | 3709.3545 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8028.99 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 | 801.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:53 | 2009-10-12 04:17 | 2009-10-12 04:41
2009-10-12 03:05 | 60.022 | 3707.696 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8029.32 | 1 | 1 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 802 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:29 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:42
2009-10-12 03:05 | 60.023 | 3707.3804 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8029.65 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 802.5 | 10 | 0 | 2009-10-12 03:05 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:42
2009-10-12 03:06 | 60.024 | 3707.1201 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8029.98 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 803 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:42
2009-10-12 03:06 | 60.026 | 3706.99 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8030.31 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 803.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:42
2009-10-12 03:06 | 60.026 | 3705.8481 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8030.64 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 804 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:42
2009-10-12 03:06 | 60.024 | 3704.1851 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8030.97 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 | 804.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:42
2009-10-12 03:06 | 60.022 | 3704.4058 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8031.3 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 805 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:42
2009-10-12 03:06 | 60.02 | 3704.9626 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8031.63 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 805.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:42
2009-10-12 03:06 | 60.019 | 3706.5674 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8031.96 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 806 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:42
2009-10-12 03:06 | 60.022 | 3705.5159 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8032.29 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 806.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:42
2009-10-12 03:06 | 60.025 | 3704.8687 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8032.62 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 807 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:43
2009-10-12 03:06 | 60.028 | 3704.4285 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8032.95 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 807.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:18 | 2009-10-12 04:43
2009-10-12 03:06 | 60.03 | 3704.7734 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8033.28 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 808 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:19 | 2009-10-12 04:43
2009-10-12 03:06 | 60.031 | 3703.5317 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8033.61 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 808.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:19 | 2009-10-12 04:43
2009-10-12 03:06 | 60.029 | 3702.6855 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8033.94 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 809 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:54 | 2009-10-12 04:19 | 2009-10-12 04:43
2009-10-12 03:06 | 60.026 | 3702.093 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8034.27 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 809.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:55 | 2009-10-12 04:19 | 2009-10-12 04:43
2009-10-12 03:06 | 60.026 | 3703.1692 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8034.6 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 810 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:55 | 2009-10-12 04:19 | 2009-10-12 04:43
2009-10-12 03:06 | 60.029 | 3703.6755 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8034.93 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 810.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:55 | 2009-10-12 04:19 | 2009-10-12 04:43
2009-10-12 03:06 | 60.03 | 3701.5195 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8035.26 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 811 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:55 | 2009-10-12 04:19 | 2009-10-12 04:43
2009-10-12 03:06 | 60.033 | 3700.1062 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8035.59 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 811.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:55 | 2009-10-12 04:19 | 2009-10-12 04:43
2009-10-12 03:06 | 60.03 | 3698.2217 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8035.92 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 812 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:30 | 2009-10-12 03:55 | 2009-10-12 04:19 | 2009-10-12 04:44
2009-10-12 03:06 | 60.022 | 3698.0088 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8036.25 | 1 | 1 | 1 | -0.0079994 | 0.0079994 |  | 350 | -223.0157 | 16 | 812.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:31 | 2009-10-12 03:55 | 2009-10-12 04:19 | 2009-10-12 04:44
2009-10-12 03:06 | 60.016 | 3700.2798 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8036.58 | 1 | 1 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 813 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:31 | 2009-10-12 03:55 | 2009-10-12 04:19 | 2009-10-12 04:44
2009-10-12 03:06 | 60.019 | 3703.1924 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8036.91 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 813.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:31 | 2009-10-12 03:55 | 2009-10-12 04:19 | 2009-10-12 04:44
2009-10-12 03:06 | 60.03 | 3703.8147 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8037.24 | 1 | 1 | 1 | 0.010998 | 0.010998 |  | 350 | -223.0157 | 16 | 814 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:31 | 2009-10-12 03:55 | 2009-10-12 04:20 | 2009-10-12 04:44
2009-10-12 03:06 | 60.028 | 3701.8633 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8037.57 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 814.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:31 | 2009-10-12 03:55 | 2009-10-12 04:20 | 2009-10-12 04:44
2009-10-12 03:06 | 60.021 | 3699.9561 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8037.9 | 1 | 1 | 1 | -0.007 | 0.007 |  | 350 | -223.0157 | 16 | 815 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:31 | 2009-10-12 03:55 | 2009-10-12 04:20 | 2009-10-12 04:44
2009-10-12 03:06 | 60.015 | 3700.8157 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8038.23 | 1 | 1 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 815.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:31 | 2009-10-12 03:55 | 2009-10-12 04:20 | 2009-10-12 04:44
2009-10-12 03:06 | 60.015 | 3703.8022 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8038.56 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 816 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:31 | 2009-10-12 03:55 | 2009-10-12 04:20 | 2009-10-12 04:44
2009-10-12 03:06 | 60.012 | 3706.9434 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8038.89 | 1 | 1 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 816.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:31 | 2009-10-12 03:55 | 2009-10-12 04:20 | 2009-10-12 04:44
2009-10-12 03:06 | 60.011 | 3708.5273 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8039.22 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 817 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:31 | 2009-10-12 03:56 | 2009-10-12 04:20 | 2009-10-12 04:45
2009-10-12 03:06 | 60.014 | 3707.4895 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8039.55 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 817.5 | 10 | 0 | 2009-10-12 03:06 | 2009-10-12 03:31 | 2009-10-12 03:56 | 2009-10-12 04:20 | 2009-10-12 04:45
2009-10-12 03:07 | 60.013 | 3707.6475 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8039.88 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 818 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:31 | 2009-10-12 03:56 | 2009-10-12 04:20 | 2009-10-12 04:45
2009-10-12 03:07 | 60.014 | 3706.9912 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8040.21 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 818.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:31 | 2009-10-12 03:56 | 2009-10-12 04:20 | 2009-10-12 04:45
2009-10-12 03:07 | 60.016 | 3707.4949 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8040.54 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 819 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:31 | 2009-10-12 03:56 | 2009-10-12 04:20 | 2009-10-12 04:45
2009-10-12 03:07 | 60.016 | 3705.5845 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8040.87 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 819.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:31 | 2009-10-12 03:56 | 2009-10-12 04:20 | 2009-10-12 04:45
2009-10-12 03:07 | 60.015 | 3705.3979 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8041.2 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 820 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:31 | 2009-10-12 03:56 | 2009-10-12 04:21 | 2009-10-12 04:45
2009-10-12 03:07 | 60.013 | 3707.1201 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8041.53 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 820.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:31 | 2009-10-12 03:56 | 2009-10-12 04:21 | 2009-10-12 04:45
2009-10-12 03:07 | 60.007 | 3709.144 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8041.86 | 1 | 1 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 | 821 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:31 | 2009-10-12 03:56 | 2009-10-12 04:21 | 2009-10-12 04:45
2009-10-12 03:07 | 59.997 | 3708.9895 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8042.19 | 1 | 0 | 1 | -0.0099983 | 0.0099983 |  | 350 | -223.0157 | 16 | 821.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:31 | 2009-10-12 03:56 | 2009-10-12 04:21 | 2009-10-12 04:45
2009-10-12 03:07 | 59.994 | 3708.291 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8042.52 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 822 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:31 | 2009-10-12 03:56 | 2009-10-12 04:21 | 2009-10-12 04:46
2009-10-12 03:07 | 59.993 | 3706.1926 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8042.85 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 822.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:56 | 2009-10-12 04:21 | 2009-10-12 04:46
2009-10-12 03:07 | 59.99 | 3707.3037 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8043.18 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 823 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:56 | 2009-10-12 04:21 | 2009-10-12 04:46
2009-10-12 03:07 | 59.993 | 3707.9033 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8043.51 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 823.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:56 | 2009-10-12 04:21 | 2009-10-12 04:46
2009-10-12 03:07 | 59.994 | 3706.7603 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8043.84 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 824 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:56 | 2009-10-12 04:21 | 2009-10-12 04:46
2009-10-12 03:07 | 59.993 | 3706.9211 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8044.17 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 824.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:21 | 2009-10-12 04:46
2009-10-12 03:07 | 59.994 | 3706.6831 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8044.5 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 825 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:21 | 2009-10-12 04:46
2009-10-12 03:07 | 59.993 | 3706.8879 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8044.83 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 825.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:21 | 2009-10-12 04:46
2009-10-12 03:07 | 59.996 | 3704.9336 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8045.16 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 826 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:46
2009-10-12 03:07 | 59.988 | 3705.6777 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8045.49 | 1 | 0 | 1 | -0.0079994 | 0.0079994 |  | 350 | -223.0157 | 16 | 826.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:46
2009-10-12 03:07 | 59.985 | 3706.481 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8045.82 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 827 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:47
2009-10-12 03:07 | 59.983 | 3707.0713 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8046.15 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 827.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:47
2009-10-12 03:07 | 59.982 | 3706.6963 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8046.48 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 | 828 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:47
2009-10-12 03:07 | 59.98 | 3707.4785 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8046.81 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 828.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:47
2009-10-12 03:07 | 59.977 | 3708.2458 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8047.14 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 829 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:47
2009-10-12 03:07 | 59.981 | 3709.4358 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8047.47 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 829.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:47
2009-10-12 03:07 | 59.982 | 3710.4194 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8047.8 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 830 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:47
2009-10-12 03:07 | 59.978 | 3710.1338 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8048.13 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 | 830.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:47
2009-10-12 03:07 | 59.98 | 3708.7078 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8048.46 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 831 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:47
2009-10-12 03:07 | 59.98 | 3710.0239 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8048.79 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 831.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:57 | 2009-10-12 04:22 | 2009-10-12 04:47
2009-10-12 03:07 | 59.977 | 3709.1919 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8049.12 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 832 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:32 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:48
2009-10-12 03:07 | 59.98 | 3708.3354 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8049.45 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 | 832.5 | 10 | 0 | 2009-10-12 03:07 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:48
2009-10-12 03:08 | 59.983 | 3709.3994 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8049.78 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 833 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:48
2009-10-12 03:08 | 59.984 | 3707.9114 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8050.11 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 833.5 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:48
2009-10-12 03:08 | 59.981 | 3709.0039 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8050.44 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 | 834 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:48
2009-10-12 03:08 | 59.981 | 3707.6382 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8050.77 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 834.5 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:48
2009-10-12 03:08 | 59.98 | 3709.689 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 8051.1 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 835 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:48
2009-10-12 03:08 | 59.981 | 3708.9453 | 350 | -223.0157 | 16 |  |  |  | -103 | 8051.43 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 835.5 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:48
2009-10-12 03:08 | 59.981 | 3706.541 | 350 | -223.0157 | 16 |  |  |  | -103 | 8051.76 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 836 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:48
2009-10-12 03:08 | 59.981 | 3711.2563 | 350 | -223.0157 | 16 |  |  |  | -103 | 8052.09 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 836.5 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:48
2009-10-12 03:08 | 59.98 | 3711.3621 | 350 | -223.0157 | 16 |  |  |  | -103 | 8052.42 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 837 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:49
2009-10-12 03:08 | 59.978 | 3712.3032 | 350 | -223.0157 | 16 |  |  |  | -103 | 8052.75 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 | 837.5 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:23 | 2009-10-12 04:49
2009-10-12 03:08 | 59.978 | 3712.0122 | 350 | -223.0157 | 16 |  |  |  | -103 | 8053.08 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 | 838 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:24 | 2009-10-12 04:49
2009-10-12 03:08 | 59.979 | 3711.7034 | 350 | -223.0157 | 16 |  |  |  | -103 | 8053.41 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 838.5 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:24 | 2009-10-12 04:49
2009-10-12 03:08 | 59.978 | 3712.0928 | 350 | -223.0157 | 16 |  |  |  | -103 | 8053.74 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 | 839 | 10 | 0 | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:58 | 2009-10-12 04:24 | 2009-10-12 04:49
2009-10-12 03:08 | 59.976 | 3713.9917 | 350 | -223.0157 | 16 |  |  |  | -103 | 8054.07 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:59 | 2009-10-12 04:24 | 2009-10-12 04:49
2009-10-12 03:08 | 59.976 | 3714.6121 | 350 | -223.0157 | 16 |  |  |  | -103 | 8054.4 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:59 | 2009-10-12 04:24 | 2009-10-12 04:49
2009-10-12 03:08 | 59.975 | 3715.0835 | 350 | -223.0157 | 16 |  |  |  | -103 | 8054.73 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:59 | 2009-10-12 04:24 | 2009-10-12 04:49
2009-10-12 03:08 | 59.976 | 3715.3228 | 350 | -223.0157 | 16 |  |  |  | -103 | 8055.06 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:59 | 2009-10-12 04:24 | 2009-10-12 04:49
2009-10-12 03:08 | 59.975 | 3714.7939 | 350 | -223.0157 | 16 |  |  |  | -103 | 8055.39 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:59 | 2009-10-12 04:24 | 2009-10-12 04:49
2009-10-12 03:08 | 59.979 | 3714.7173 | 350 | -223.0157 | 16 |  |  |  | -103 | 8055.72 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:33 | 2009-10-12 03:59 | 2009-10-12 04:24 | 2009-10-12 04:50
2009-10-12 03:08 | 59.978 | 3715.1614 | 350 | -223.0157 | 16 |  |  |  | -103 | 8056.05 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:34 | 2009-10-12 03:59 | 2009-10-12 04:24 | 2009-10-12 04:50
2009-10-12 03:08 | 59.975 | 3715.0012 | 350 | -223.0157 | 16 |  |  |  | -103 | 8056.38 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:34 | 2009-10-12 03:59 | 2009-10-12 04:24 | 2009-10-12 04:50
2009-10-12 03:08 | 59.976 | 3713.9963 | 350 | -223.0157 | 16 |  |  |  | -103 | 8056.71 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:34 | 2009-10-12 03:59 | 2009-10-12 04:24 | 2009-10-12 04:50
2009-10-12 03:08 | 59.981 | 3714.0627 | 350 | -223.0157 | 16 |  |  |  | -103 | 8057.04 | 1 | 0 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:34 | 2009-10-12 03:59 | 2009-10-12 04:25 | 2009-10-12 04:50
2009-10-12 03:08 | 59.977 | 3714.3347 | 350 | -223.0157 | 16 |  |  |  | -103 | 8057.37 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:34 | 2009-10-12 03:59 | 2009-10-12 04:25 | 2009-10-12 04:50
2009-10-12 03:08 | 59.975 | 3715.6311 | 350 | -223.0157 | 16 |  |  |  | -103 | 8057.7 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:34 | 2009-10-12 03:59 | 2009-10-12 04:25 | 2009-10-12 04:50
2009-10-12 03:08 | 59.976 | 3715.6885 | 350 | -223.0157 | 16 |  |  |  | -103 | 8058.03 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:34 | 2009-10-12 03:59 | 2009-10-12 04:25 | 2009-10-12 04:50
2009-10-12 03:08 | 59.979 | 3715.5674 | 350 | -223.0157 | 16 |  |  |  | -103 | 8058.36 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:34 | 2009-10-12 03:59 | 2009-10-12 04:25 | 2009-10-12 04:50
2009-10-12 03:08 | 59.98 | 3715.7246 | 350 | -223.0157 | 16 |  |  |  | -103 | 8058.69 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:34 | 2009-10-12 03:59 | 2009-10-12 04:25 | 2009-10-12 04:50
2009-10-12 03:08 | 59.979 | 3714.8481 | 350 | -223.0157 | 16 |  |  |  | -103 | 8059.02 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:34 | 2009-10-12 04:00 | 2009-10-12 04:25 | 2009-10-12 04:51
2009-10-12 03:08 | 59.978 | 3713.1416 | 350 | -223.0157 | 16 |  |  |  | -103 | 8059.35 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:08 | 2009-10-12 03:34 | 2009-10-12 04:00 | 2009-10-12 04:25 | 2009-10-12 04:51
2009-10-12 03:09 | 59.979 | 3713.3584 | 350 | -223.0157 | 16 |  |  |  | -103 | 8059.68 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:34 | 2009-10-12 04:00 | 2009-10-12 04:25 | 2009-10-12 04:51
2009-10-12 03:09 | 59.982 | 3712.2747 | 350 | -223.0157 | 16 |  |  |  | -103 | 8060.01 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:34 | 2009-10-12 04:00 | 2009-10-12 04:25 | 2009-10-12 04:51
2009-10-12 03:09 | 59.983 | 3712.6194 | 350 | -223.0157 | 16 |  |  |  | -103 | 8060.34 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:34 | 2009-10-12 04:00 | 2009-10-12 04:25 | 2009-10-12 04:51
2009-10-12 03:09 | 59.987 | 3712.1526 | 350 | -223.0157 | 16 |  |  |  | -103 | 8060.67 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:34 | 2009-10-12 04:00 | 2009-10-12 04:25 | 2009-10-12 04:51
2009-10-12 03:09 | 59.988 | 3710.0503 | 350 | -223.0157 | 16 |  |  |  | -103 | 8061 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:34 | 2009-10-12 04:00 | 2009-10-12 04:26 | 2009-10-12 04:51
2009-10-12 03:09 | 59.984 | 3709.0815 | 350 | -223.0157 | 16 |  |  |  | -103 | 8061.33 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:34 | 2009-10-12 04:00 | 2009-10-12 04:26 | 2009-10-12 04:51
2009-10-12 03:09 | 59.98 | 3710.4719 | 350 | -223.0157 | 16 |  |  |  | -103 | 8061.66 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:34 | 2009-10-12 04:00 | 2009-10-12 04:26 | 2009-10-12 04:51
2009-10-12 03:09 | 59.979 | 3710.6235 | 350 | -223.0157 | 16 |  |  |  | -103 | 8061.99 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:34 | 2009-10-12 04:00 | 2009-10-12 04:26 | 2009-10-12 04:51
2009-10-12 03:09 | 59.98 | 3710.9463 | 350 | -223.0157 | 16 |  |  |  | -103 | 8062.32 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:34 | 2009-10-12 04:00 | 2009-10-12 04:26 | 2009-10-12 04:52
2009-10-12 03:09 | 59.979 | 3710.1997 | 350 | -223.0157 | 16 |  |  |  | -103 | 8062.65 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:00 | 2009-10-12 04:26 | 2009-10-12 04:52
2009-10-12 03:09 | 59.978 | 3710.4746 | 350 | -223.0157 | 16 |  |  |  | -103 | 8062.98 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:00 | 2009-10-12 04:26 | 2009-10-12 04:52
2009-10-12 03:09 | 59.975 | 3709.4622 | 350 | -223.0157 | 16 |  |  |  | -103 | 8063.31 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:00 | 2009-10-12 04:26 | 2009-10-12 04:52
2009-10-12 03:09 | 59.979 | 3710.803 | 350 | -223.0157 | 16 |  |  |  | -103 | 8063.64 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:00 | 2009-10-12 04:26 | 2009-10-12 04:52
2009-10-12 03:09 | 59.982 | 3709.2859 | 350 | -223.0157 | 16 |  |  |  | -103 | 8063.97 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:26 | 2009-10-12 04:52
2009-10-12 03:09 | 59.983 | 3710.573 | 350 | -223.0157 | 16 |  |  |  | -103 | 8064.3 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:26 | 2009-10-12 04:52
2009-10-12 03:09 | 59.983 | 3709.5251 | 350 | -223.0157 | 16 |  |  |  | -103 | 8064.63 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:26 | 2009-10-12 04:52
2009-10-12 03:09 | 59.985 | 3708.3711 | 350 | -223.0157 | 16 |  |  |  | -103 | 8064.96 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:52
2009-10-12 03:09 | 59.99 | 3708.5273 | 350 | -223.0157 | 16 |  |  |  | -103 | 8065.29 | 1 | 0 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:52
2009-10-12 03:09 | 59.987 | 3706.512 | 350 | -223.0157 | 16 |  |  |  | -103 | 8065.62 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:53
2009-10-12 03:09 | 59.984 | 3707.4905 | 350 | -223.0157 | 16 |  |  |  | -103 | 8065.95 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:53
2009-10-12 03:09 | 59.976 | 3708.9624 | 350 | -223.0157 | 16 |  |  |  | -103 | 8066.28 | 1 | 0 | 1 | -0.0079994 | 0.0079994 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:53
2009-10-12 03:09 | 59.979 | 3709.894 | 350 | -223.0157 | 16 |  |  |  | -103 | 8066.61 | 1 | 0 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:53
2009-10-12 03:09 | 59.985 | 3712.3035 | 350 | -223.0157 | 16 |  |  |  | -103 | 8066.94 | 1 | 0 | 1 | 0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:53
2009-10-12 03:09 | 59.983 | 3711.3501 | 350 | -223.0157 | 16 |  |  |  | -103 | 8067.27 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:53
2009-10-12 03:09 | 59.979 | 3711.6272 | 350 | -223.0157 | 16 |  |  |  | -103 | 8067.6 | 1 | 0 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:53
2009-10-12 03:09 | 59.981 | 3712.0762 | 350 | -223.0157 | 16 |  |  |  | -103 | 8067.93 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:53
2009-10-12 03:09 | 59.978 | 3712.3926 | 350 | -223.0157 | 16 |  |  |  | -103 | 8068.26 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:53
2009-10-12 03:09 | 59.975 | 3712.9985 | 350 | -223.0157 | 16 |  |  |  | -103 | 8068.59 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:01 | 2009-10-12 04:27 | 2009-10-12 04:53
2009-10-12 03:09 | 59.978 | 3713.5103 | 350 | -223.0157 | 16 |  |  |  | -103 | 8068.92 | 1 | 0 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:35 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:54
2009-10-12 03:09 | 59.989 | 3716.6257 | 350 | -223.0157 | 16 |  |  |  | -103 | 8069.25 | 1 | 0 | 1 | 0.010998 | 0.010998 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:09 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:54
2009-10-12 03:10 | 59.999 | 3715.4429 | 350 | -223.0157 | 16 |  |  |  | -103 | 8069.58 | 1 | 0 | 1 | 0.010002 | 0.010002 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:54
2009-10-12 03:10 | 59.994 | 3712.0918 | 350 | -223.0157 | 16 |  |  |  | -103 | 8069.91 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:54
2009-10-12 03:10 | 59.989 | 3713.906 | 350 | -223.0157 | 16 |  |  |  | -103 | 8070.24 | 1 | 0 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:54
2009-10-12 03:10 | 59.986 | 3714.8936 | 350 | -223.0157 | 16 |  |  |  | -103 | 8070.57 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:54
2009-10-12 03:10 | 59.984 | 3714.9531 | 350 | -223.0157 | 16 |  |  |  | -103 | 8070.9 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:54
2009-10-12 03:10 | 59.983 | 3716.1216 | 350 | -223.0157 | 16 |  |  |  | -103 | 8071.23 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:54
2009-10-12 03:10 | 59.982 | 3716.3083 | 350 | -223.0157 | 16 |  |  |  | -103 | 8071.56 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:54
2009-10-12 03:10 | 59.98 | 3715.4385 | 350 | -223.0157 | 16 |  |  |  | -103 | 8071.89 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:54
2009-10-12 03:10 | 59.99 | 3714.7637 | 350 | -223.0157 | 16 |  |  |  | -103 | 8072.22 | 1 | 0 | 1 | 0.010002 | 0.010002 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:55
2009-10-12 03:10 | 59.995 | 3714.7141 | 350 | -223.0157 | 16 |  |  |  | -103 | 8072.55 | 1 | 0 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:28 | 2009-10-12 04:55
2009-10-12 03:10 | 59.995 | 3715.0676 | 350 | -223.0157 | 16 |  |  |  | -103 | 8072.88 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:29 | 2009-10-12 04:55
2009-10-12 03:10 | 59.99 | 3715.9268 | 350 | -223.0157 | 16 |  |  |  | -103 | 8073.21 | 1 | 0 | 1 | -0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:29 | 2009-10-12 04:55
2009-10-12 03:10 | 59.989 | 3715.7913 | 350 | -223.0157 | 16 |  |  |  | -103 | 8073.54 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:02 | 2009-10-12 04:29 | 2009-10-12 04:55
2009-10-12 03:10 | 59.991 | 3716.2847 | 350 | -223.0157 | 16 |  |  |  | -103 | 8073.87 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:03 | 2009-10-12 04:29 | 2009-10-12 04:55
2009-10-12 03:10 | 59.996 | 3715.3245 | 350 | -223.0157 | 16 |  |  |  | -103 | 8074.2 | 1 | 0 | 1 | 0.0049973 | 0.0049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:03 | 2009-10-12 04:29 | 2009-10-12 04:55
2009-10-12 03:10 | 60 | 3714.4604 | 350 | -223.0157 | 16 |  |  |  | -103 | 8074.53 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:03 | 2009-10-12 04:29 | 2009-10-12 04:55
2009-10-12 03:10 | 60.002 | 3711.7085 | 350 | -223.0157 | 16 |  |  |  | -103 | 8074.86 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:03 | 2009-10-12 04:29 | 2009-10-12 04:55
2009-10-12 03:10 | 60.004 | 3712.6975 | 350 | -223.0157 | 16 |  |  |  | -103 | 8075.19 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:03 | 2009-10-12 04:29 | 2009-10-12 04:55
2009-10-12 03:10 | 60.004 | 3712.8506 | 350 | -223.0157 | 16 |  |  |  | -103 | 8075.52 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:36 | 2009-10-12 04:03 | 2009-10-12 04:29 | 2009-10-12 04:56
2009-10-12 03:10 | 60.002 | 3713.3616 | 350 | -223.0157 | 16 |  |  |  | -103 | 8075.85 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:37 | 2009-10-12 04:03 | 2009-10-12 04:29 | 2009-10-12 04:56
2009-10-12 03:10 | 59.999 | 3716.6414 | 350 | -223.0157 | 16 |  |  |  | -103 | 8076.18 | 1 | 0 | 1 | -0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:37 | 2009-10-12 04:03 | 2009-10-12 04:29 | 2009-10-12 04:56
2009-10-12 03:10 | 59.998 | 3718.2925 | 350 | -223.0157 | 16 |  |  |  | -103 | 8076.51 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:37 | 2009-10-12 04:03 | 2009-10-12 04:29 | 2009-10-12 04:56
2009-10-12 03:10 | 59.995 | 3719.0791 | 350 | -223.0157 | 16 |  |  |  | -103 | 8076.84 | 1 | 0 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:37 | 2009-10-12 04:03 | 2009-10-12 04:30 | 2009-10-12 04:56
2009-10-12 03:10 | 59.996 | 3718.2334 | 350 | -223.0157 | 16 |  |  |  | -103 | 8077.17 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:37 | 2009-10-12 04:03 | 2009-10-12 04:30 | 2009-10-12 04:56
2009-10-12 03:10 | 60.001 | 3717.8152 | 350 | -223.0157 | 16 |  |  |  | -103 | 8077.5 | 1 | 1 | 1 | 0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:37 | 2009-10-12 04:03 | 2009-10-12 04:30 | 2009-10-12 04:56
2009-10-12 03:10 | 60.002 | 3717.8887 | 350 | -223.0157 | 16 |  |  |  | -103 | 8077.83 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:37 | 2009-10-12 04:03 | 2009-10-12 04:30 | 2009-10-12 04:56
2009-10-12 03:10 | 60.001 | 3718.5603 | 350 | -223.0157 | 16 |  |  |  | -103 | 8078.16 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:37 | 2009-10-12 04:03 | 2009-10-12 04:30 | 2009-10-12 04:56
2009-10-12 03:10 | 60.003 | 3718.1953 | 350 | -223.0157 | 16 |  |  |  | -103 | 8078.49 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:37 | 2009-10-12 04:03 | 2009-10-12 04:30 | 2009-10-12 04:56
2009-10-12 03:10 | 60.005 | 3719.0212 | 350 | -223.0157 | 16 |  |  |  | -103 | 8078.82 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:37 | 2009-10-12 04:04 | 2009-10-12 04:30 | 2009-10-12 04:57
2009-10-12 03:10 | 60.004 | 3718.8213 | 350 | -223.0157 | 16 |  |  |  | -103 | 8079.15 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:10 | 2009-10-12 03:37 | 2009-10-12 04:04 | 2009-10-12 04:30 | 2009-10-12 04:57
2009-10-12 03:11 | 60.004 | 3719.8975 | 350 | -223.0157 | 16 |  |  |  | -103 | 8079.48 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:37 | 2009-10-12 04:04 | 2009-10-12 04:30 | 2009-10-12 04:57
2009-10-12 03:11 | 60.004 | 3719.2993 | 350 | -223.0157 | 16 |  |  |  | -103 | 8079.81 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:37 | 2009-10-12 04:04 | 2009-10-12 04:30 | 2009-10-12 04:57
2009-10-12 03:11 | 60.006 | 3719.6428 | 350 | -223.0157 | 16 |  |  |  | -103 | 8080.14 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:37 | 2009-10-12 04:04 | 2009-10-12 04:30 | 2009-10-12 04:57
2009-10-12 03:11 | 60.003 | 3719.5273 | 350 | -223.0157 | 16 |  |  |  | -103 | 8080.47 | 1 | 1 | 1 | -0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:37 | 2009-10-12 04:04 | 2009-10-12 04:30 | 2009-10-12 04:57
2009-10-12 03:11 | 60.005 | 3719.731 | 350 | -223.0157 | 16 |  |  |  | -103 | 8080.8 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:37 | 2009-10-12 04:04 | 2009-10-12 04:31 | 2009-10-12 04:57
2009-10-12 03:11 | 60.006 | 3720.2786 | 350 | -223.0157 | 16 |  |  |  | -103 | 8081.13 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:37 | 2009-10-12 04:04 | 2009-10-12 04:31 | 2009-10-12 04:57
2009-10-12 03:11 | 60.009 | 3718.5796 | 350 | -223.0157 | 16 |  |  |  | -103 | 8081.46 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:37 | 2009-10-12 04:04 | 2009-10-12 04:31 | 2009-10-12 04:57
2009-10-12 03:11 | 60.009 | 3718.9761 | 350 | -223.0157 | 16 |  |  |  | -103 | 8081.79 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:37 | 2009-10-12 04:04 | 2009-10-12 04:31 | 2009-10-12 04:57
2009-10-12 03:11 | 60.01 | 3718.9822 | 350 | -223.0157 | 16 |  |  |  | -103 | 8082.12 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:37 | 2009-10-12 04:04 | 2009-10-12 04:31 | 2009-10-12 04:58
2009-10-12 03:11 | 60.009 | 3720.0337 | 350 | -223.0157 | 16 |  |  |  | -103 | 8082.45 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:04 | 2009-10-12 04:31 | 2009-10-12 04:58
2009-10-12 03:11 | 60.013 | 3720.6089 | 350 | -223.0157 | 16 |  |  |  | -103 | 8082.78 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:04 | 2009-10-12 04:31 | 2009-10-12 04:58
2009-10-12 03:11 | 60.015 | 3720.8105 | 350 | -223.0157 | 16 |  |  |  | -103 | 8083.11 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:04 | 2009-10-12 04:31 | 2009-10-12 04:58
2009-10-12 03:11 | 60.014 | 3721.2388 | 350 | -223.0157 | 16 |  |  |  | -103 | 8083.44 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:04 | 2009-10-12 04:31 | 2009-10-12 04:58
2009-10-12 03:11 | 60.009 | 3720.3804 | 350 | -223.0157 | 16 |  |  |  | -103 | 8083.77 | 1 | 1 | 1 | -0.0050011 | 0.0050011 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:31 | 2009-10-12 04:58
2009-10-12 03:11 | 60.009 | 3719.4473 | 350 | -223.0157 | 16 |  |  |  | -103 | 8084.1 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:31 | 2009-10-12 04:58
2009-10-12 03:11 | 60.008 | 3720.8071 | 350 | -223.0157 | 16 |  |  |  | -103 | 8084.43 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:31 | 2009-10-12 04:58
2009-10-12 03:11 | 60.011 | 3721.2722 | 350 | -223.0157 | 16 |  |  |  | -103 | 8084.76 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:58
2009-10-12 03:11 | 60.01 | 3720.5916 | 350 | -223.0157 | 16 |  |  |  | -103 | 8085.09 | 1 | 1 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:58
2009-10-12 03:11 | 60.009 | 3721.2446 | 350 | -223.0157 | 16 |  |  |  | -103 | 8085.42 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:59
2009-10-12 03:11 | 60.013 | 3721.5938 | 350 | -223.0157 | 16 |  |  |  | -103 | 8085.75 | 1 | 1 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:59
2009-10-12 03:11 | 60.013 | 3722.1763 | 350 | -223.0157 | 16 |  |  |  | -103 | 8086.08 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:59
2009-10-12 03:11 | 60.014 | 3721.999 | 350 | -223.0157 | 16 |  |  |  | -103 | 8086.41 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:59
2009-10-12 03:11 | 60.014 | 3721.646 | 350 | -223.0157 | 16 |  |  |  | -103 | 8086.74 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:59
2009-10-12 03:11 | 60.012 | 3721.6777 | 350 | -223.0157 | 16 |  |  |  | -103 | 8087.07 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:59
2009-10-12 03:11 | 60.01 | 3720.8596 | 350 | -223.0157 | 16 |  |  |  | -103 | 8087.4 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:59
2009-10-12 03:11 | 60.011 | 3721.6453 | 350 | -223.0157 | 16 |  |  |  | -103 | 8087.73 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:59
2009-10-12 03:11 | 60.007 | 3723.8157 | 350 | -223.0157 | 16 |  |  |  | -103 | 8088.06 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:59
2009-10-12 03:11 | 60.003 | 3725.0703 | 350 | -223.0157 | 16 |  |  |  | -103 | 8088.39 | 1 | 1 | 1 | -0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:05 | 2009-10-12 04:32 | 2009-10-12 04:59
2009-10-12 03:11 | 60.001 | 3724.656 | 350 | -223.0157 | 16 |  |  |  | -103 | 8088.72 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:38 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:00
2009-10-12 03:11 | 60 | 3724.8694 | 350 | -223.0157 | 16 |  |  |  | -103 | 8089.05 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:11 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:00
2009-10-12 03:12 | 59.998 | 3724.6606 | 350 | -223.0157 | 16 |  |  |  | -103 | 8089.38 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:00
2009-10-12 03:12 | 59.998 | 3723.696 | 350 | -223.0157 | 16 |  |  |  | -103 | 8089.71 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:00
2009-10-12 03:12 | 59.999 | 3723.5801 | 350 | -223.0157 | 16 |  |  |  | -103 | 8090.04 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:00
2009-10-12 03:12 | 60.002 | 3723.4053 | 350 | -223.0157 | 16 |  |  |  | -103 | 8090.37 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:00
2009-10-12 03:12 | 60.003 | 3721.8789 | 350 | -223.0157 | 16 |  |  |  | -103 | 8090.7 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:00
2009-10-12 03:12 | 60.003 | 3722.4014 | 350 | -223.0157 | 16 |  |  |  | -103 | 8091.03 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:00
2009-10-12 03:12 | 59.999 | 3722.9065 | 350 | -223.0157 | 16 |  |  |  | -103 | 8091.36 | 1 | 0 | 1 | -0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:00
2009-10-12 03:12 | 59.998 | 3724.1421 | 350 | -223.0157 | 16 |  |  |  | -103 | 8091.69 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:00
2009-10-12 03:12 | 60.001 | 3723.6504 | 350 | -223.0157 | 16 |  |  |  | -103 | 8092.02 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:01
2009-10-12 03:12 | 59.995 | 3723.2012 | 350 | -223.0157 | 16 |  |  |  | -103 | 8092.35 | 1 | 0 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:33 | 2009-10-12 05:01
2009-10-12 03:12 | 59.989 | 3723.6389 | 350 | -223.0157 | 16 |  |  |  | -103 | 8092.68 | 1 | 0 | 1 | -0.0060005 | 0.0060005 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:34 | 2009-10-12 05:01
2009-10-12 03:12 | 59.987 | 3723.8813 | 350 | -223.0157 | 16 |  |  |  | -103 | 8093.01 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:34 | 2009-10-12 05:01
2009-10-12 03:12 | 59.988 | 3724.6543 | 350 | -223.0157 | 16 |  |  |  | -103 | 8093.34 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:06 | 2009-10-12 04:34 | 2009-10-12 05:01
2009-10-12 03:12 | 59.988 | 3725.3608 | 350 | -223.0157 | 16 |  |  |  | -103 | 8093.67 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:07 | 2009-10-12 04:34 | 2009-10-12 05:01
2009-10-12 03:12 | 59.99 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:07 | 2009-10-12 04:34 | 2009-10-12 05:01
2009-10-12 03:12 | 59.999 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.0089989 | 0.0089989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:07 | 2009-10-12 04:34 | 2009-10-12 05:01
2009-10-12 03:12 | 60.001 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:07 | 2009-10-12 04:34 | 2009-10-12 05:01
2009-10-12 03:12 | 60.003 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:07 | 2009-10-12 04:34 | 2009-10-12 05:01
2009-10-12 03:12 | 60.0005 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.0024986 | 0.0024986 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:39 | 2009-10-12 04:07 | 2009-10-12 04:34 | 2009-10-12 05:02
2009-10-12 03:12 | 59.998 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0024986 | 0.0024986 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:40 | 2009-10-12 04:07 | 2009-10-12 04:34 | 2009-10-12 05:02
2009-10-12 03:12 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:40 | 2009-10-12 04:07 | 2009-10-12 04:34 | 2009-10-12 05:02
2009-10-12 03:12 | 59.996 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:40 | 2009-10-12 04:07 | 2009-10-12 04:34 | 2009-10-12 05:02
2009-10-12 03:12 | 59.996 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:40 | 2009-10-12 04:07 | 2009-10-12 04:35 | 2009-10-12 05:02
2009-10-12 03:12 | 59.996 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:40 | 2009-10-12 04:07 | 2009-10-12 04:35 | 2009-10-12 05:02
2009-10-12 03:12 | 59.995 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:40 | 2009-10-12 04:07 | 2009-10-12 04:35 | 2009-10-12 05:02
2009-10-12 03:12 | 59.994 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:40 | 2009-10-12 04:07 | 2009-10-12 04:35 | 2009-10-12 05:02
2009-10-12 03:12 | 59.993 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:40 | 2009-10-12 04:07 | 2009-10-12 04:35 | 2009-10-12 05:02
2009-10-12 03:12 | 59.992 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:40 | 2009-10-12 04:07 | 2009-10-12 04:35 | 2009-10-12 05:02
2009-10-12 03:12 | 59.991 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:40 | 2009-10-12 04:08 | 2009-10-12 04:35 | 2009-10-12 05:03
2009-10-12 03:12 | 59.99 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:12 | 2009-10-12 03:40 | 2009-10-12 04:08 | 2009-10-12 04:35 | 2009-10-12 05:03
2009-10-12 03:13 | 59.991 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:40 | 2009-10-12 04:08 | 2009-10-12 04:35 | 2009-10-12 05:03
2009-10-12 03:13 | 59.992 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:40 | 2009-10-12 04:08 | 2009-10-12 04:35 | 2009-10-12 05:03
2009-10-12 03:13 | 59.993 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:40 | 2009-10-12 04:08 | 2009-10-12 04:35 | 2009-10-12 05:03
2009-10-12 03:13 | 59.994 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:40 | 2009-10-12 04:08 | 2009-10-12 04:35 | 2009-10-12 05:03
2009-10-12 03:13 | 59.995 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:40 | 2009-10-12 04:08 | 2009-10-12 04:36 | 2009-10-12 05:03
2009-10-12 03:13 | 59.996 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:40 | 2009-10-12 04:08 | 2009-10-12 04:36 | 2009-10-12 05:03
2009-10-12 03:13 | 59.996 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:40 | 2009-10-12 04:08 | 2009-10-12 04:36 | 2009-10-12 05:03
2009-10-12 03:13 | 59.996 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:40 | 2009-10-12 04:08 | 2009-10-12 04:36 | 2009-10-12 05:03
2009-10-12 03:13 | 59.9965 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:40 | 2009-10-12 04:08 | 2009-10-12 04:36 | 2009-10-12 05:04
2009-10-12 03:13 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00050354 | 0.00050354 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:08 | 2009-10-12 04:36 | 2009-10-12 05:04
2009-10-12 03:13 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:08 | 2009-10-12 04:36 | 2009-10-12 05:04
2009-10-12 03:13 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:08 | 2009-10-12 04:36 | 2009-10-12 05:04
2009-10-12 03:13 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:08 | 2009-10-12 04:36 | 2009-10-12 05:04
2009-10-12 03:13 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:36 | 2009-10-12 05:04
2009-10-12 03:13 | 59.999 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:36 | 2009-10-12 05:04
2009-10-12 03:13 | 60.001 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:36 | 2009-10-12 05:04
2009-10-12 03:13 | 60.001 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:04
2009-10-12 03:13 | 60.001 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:04
2009-10-12 03:13 | 60.004 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0029984 | 0.0029984 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:05
2009-10-12 03:13 | 60.007 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0030022 | 0.0030022 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:05
2009-10-12 03:13 | 60.009 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:05
2009-10-12 03:13 | 60.011 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:05
2009-10-12 03:13 | 60.0085 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.0025024 | 0.0025024 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:05
2009-10-12 03:13 | 60.006 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.0024986 | 0.0024986 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:05
2009-10-12 03:13 | 60.007 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:05
2009-10-12 03:13 | 60.008 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:05
2009-10-12 03:13 | 60.01 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:05
2009-10-12 03:13 | 60.012 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:09 | 2009-10-12 04:37 | 2009-10-12 05:05
2009-10-12 03:13 | 60.012 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:41 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:06
2009-10-12 03:13 | 60.012 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:13 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:06
2009-10-12 03:14 | 60.01 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:06
2009-10-12 03:14 | 60.008 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:06
2009-10-12 03:14 | 60.008 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:06
2009-10-12 03:14 | 60.008 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:06
2009-10-12 03:14 | 60.008 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:06
2009-10-12 03:14 | 60.008 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:06
2009-10-12 03:14 | 60.008 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:06
2009-10-12 03:14 | 60.008 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:06
2009-10-12 03:14 | 60.007 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:07
2009-10-12 03:14 | 60.006 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:38 | 2009-10-12 05:07
2009-10-12 03:14 | 60.005 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:39 | 2009-10-12 05:07
2009-10-12 03:14 | 60.004 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:39 | 2009-10-12 05:07
2009-10-12 03:14 | 60.004 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:10 | 2009-10-12 04:39 | 2009-10-12 05:07
2009-10-12 03:14 | 60.004 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:11 | 2009-10-12 04:39 | 2009-10-12 05:07
2009-10-12 03:14 | 60.0025 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:11 | 2009-10-12 04:39 | 2009-10-12 05:07
2009-10-12 03:14 | 60.001 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.001503 | 0.001503 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:11 | 2009-10-12 04:39 | 2009-10-12 05:07
2009-10-12 03:14 | 59.9995 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:11 | 2009-10-12 04:39 | 2009-10-12 05:07
2009-10-12 03:14 | 59.998 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:11 | 2009-10-12 04:39 | 2009-10-12 05:07
2009-10-12 03:14 | 59.9965 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.001503 | 0.001503 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:42 | 2009-10-12 04:11 | 2009-10-12 04:39 | 2009-10-12 05:08
2009-10-12 03:14 | 59.995 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:43 | 2009-10-12 04:11 | 2009-10-12 04:39 | 2009-10-12 05:08
2009-10-12 03:14 | 59.995 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:43 | 2009-10-12 04:11 | 2009-10-12 04:39 | 2009-10-12 05:08
2009-10-12 03:14 | 59.995 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:43 | 2009-10-12 04:11 | 2009-10-12 04:39 | 2009-10-12 05:08
2009-10-12 03:14 | 59.996 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:43 | 2009-10-12 04:11 | 2009-10-12 04:40 | 2009-10-12 05:08
2009-10-12 03:14 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:43 | 2009-10-12 04:11 | 2009-10-12 04:40 | 2009-10-12 05:08
2009-10-12 03:14 | 59.995 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:43 | 2009-10-12 04:11 | 2009-10-12 04:40 | 2009-10-12 05:08
2009-10-12 03:14 | 59.993 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:43 | 2009-10-12 04:11 | 2009-10-12 04:40 | 2009-10-12 05:08
2009-10-12 03:14 | 59.9925 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:43 | 2009-10-12 04:11 | 2009-10-12 04:40 | 2009-10-12 05:08
2009-10-12 03:14 | 59.992 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:43 | 2009-10-12 04:11 | 2009-10-12 04:40 | 2009-10-12 05:08
2009-10-12 03:14 | 59.9905 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:43 | 2009-10-12 04:12 | 2009-10-12 04:40 | 2009-10-12 05:09
2009-10-12 03:14 | 59.989 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.001503 | 0.001503 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:14 | 2009-10-12 03:43 | 2009-10-12 04:12 | 2009-10-12 04:40 | 2009-10-12 05:09
2009-10-12 03:15 | 59.99 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:43 | 2009-10-12 04:12 | 2009-10-12 04:40 | 2009-10-12 05:09
2009-10-12 03:15 | 59.991 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:43 | 2009-10-12 04:12 | 2009-10-12 04:40 | 2009-10-12 05:09
2009-10-12 03:15 | 59.989 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:43 | 2009-10-12 04:12 | 2009-10-12 04:40 | 2009-10-12 05:09
2009-10-12 03:15 | 59.987 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:43 | 2009-10-12 04:12 | 2009-10-12 04:40 | 2009-10-12 05:09
2009-10-12 03:15 | 59.9875 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:43 | 2009-10-12 04:12 | 2009-10-12 04:41 | 2009-10-12 05:09
2009-10-12 03:15 | 59.988 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:43 | 2009-10-12 04:12 | 2009-10-12 04:41 | 2009-10-12 05:09
2009-10-12 03:15 | 59.988 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:43 | 2009-10-12 04:12 | 2009-10-12 04:41 | 2009-10-12 05:09
2009-10-12 03:15 | 59.988 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:43 | 2009-10-12 04:12 | 2009-10-12 04:41 | 2009-10-12 05:09
2009-10-12 03:15 | 59.987 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:43 | 2009-10-12 04:12 | 2009-10-12 04:41 | 2009-10-12 05:10
2009-10-12 03:15 | 59.986 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:12 | 2009-10-12 04:41 | 2009-10-12 05:10
2009-10-12 03:15 | 59.9855 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:12 | 2009-10-12 04:41 | 2009-10-12 05:10
2009-10-12 03:15 | 59.985 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:12 | 2009-10-12 04:41 | 2009-10-12 05:10
2009-10-12 03:15 | 59.9845 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:12 | 2009-10-12 04:41 | 2009-10-12 05:10
2009-10-12 03:15 | 59.984 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:41 | 2009-10-12 05:10
2009-10-12 03:15 | 59.984 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:41 | 2009-10-12 05:10
2009-10-12 03:15 | 59.984 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:41 | 2009-10-12 05:10
2009-10-12 03:15 | 59.985 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:10
2009-10-12 03:15 | 59.986 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:10
2009-10-12 03:15 | 59.987 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:11
2009-10-12 03:15 | 59.988 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:11
2009-10-12 03:15 | 59.992 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.0039978 | 0.0039978 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:11
2009-10-12 03:15 | 59.996 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.0040016 | 0.0040016 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:11
2009-10-12 03:15 | 59.9975 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:11
2009-10-12 03:15 | 59.999 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.001503 | 0.001503 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:11
2009-10-12 03:15 | 60.001 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:11
2009-10-12 03:15 | 60.003 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:11
2009-10-12 03:15 | 60.003 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:11
2009-10-12 03:15 | 60.003 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:13 | 2009-10-12 04:42 | 2009-10-12 05:11
2009-10-12 03:15 | 60.0055 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0025024 | 0.0025024 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:44 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:12
2009-10-12 03:15 | 60.008 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0024986 | 0.0024986 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:15 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:12
2009-10-12 03:16 | 60.01 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0020027 | 0.0020027 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:12
2009-10-12 03:16 | 60.012 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:12
2009-10-12 03:16 | 60.0105 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.001503 | 0.001503 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:12
2009-10-12 03:16 | 60.009 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:12
2009-10-12 03:16 | 60.01 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0010033 | 0.0010033 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:12
2009-10-12 03:16 | 60.011 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:12
2009-10-12 03:16 | 60.012 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:12
2009-10-12 03:16 | 60.013 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:12
2009-10-12 03:16 | 60.013 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:13
2009-10-12 03:16 | 60.013 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:43 | 2009-10-12 05:13
2009-10-12 03:16 | 60.0145 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:44 | 2009-10-12 05:13
2009-10-12 03:16 | 60.016 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:44 | 2009-10-12 05:13
2009-10-12 03:16 | 60.0155 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:14 | 2009-10-12 04:44 | 2009-10-12 05:13
2009-10-12 03:16 | 60.015 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:15 | 2009-10-12 04:44 | 2009-10-12 05:13
2009-10-12 03:16 | 60.014 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:15 | 2009-10-12 04:44 | 2009-10-12 05:13
2009-10-12 03:16 | 60.013 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:15 | 2009-10-12 04:44 | 2009-10-12 05:13
2009-10-12 03:16 | 60.012 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:15 | 2009-10-12 04:44 | 2009-10-12 05:13
2009-10-12 03:16 | 60.011 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:15 | 2009-10-12 04:44 | 2009-10-12 05:13
2009-10-12 03:16 | 60.0105 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00050354 | 0.00050354 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:45 | 2009-10-12 04:15 | 2009-10-12 04:44 | 2009-10-12 05:14
2009-10-12 03:16 | 60.01 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:46 | 2009-10-12 04:15 | 2009-10-12 04:44 | 2009-10-12 05:14
2009-10-12 03:16 | 60.008 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:46 | 2009-10-12 04:15 | 2009-10-12 04:44 | 2009-10-12 05:14
2009-10-12 03:16 | 60.006 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:46 | 2009-10-12 04:15 | 2009-10-12 04:44 | 2009-10-12 05:14
2009-10-12 03:16 | 60.006 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:46 | 2009-10-12 04:15 | 2009-10-12 04:45 | 2009-10-12 05:14
2009-10-12 03:16 | 60.006 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:46 | 2009-10-12 04:15 | 2009-10-12 04:45 | 2009-10-12 05:14
2009-10-12 03:16 | 60.0045 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:46 | 2009-10-12 04:15 | 2009-10-12 04:45 | 2009-10-12 05:14
2009-10-12 03:16 | 60.003 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.001503 | 0.001503 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:46 | 2009-10-12 04:15 | 2009-10-12 04:45 | 2009-10-12 05:14
2009-10-12 03:16 | 60.003 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:46 | 2009-10-12 04:15 | 2009-10-12 04:45 | 2009-10-12 05:14
2009-10-12 03:16 | 60.003 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:46 | 2009-10-12 04:15 | 2009-10-12 04:45 | 2009-10-12 05:14
2009-10-12 03:16 | 60.0035 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.00050354 | 0.00050354 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:46 | 2009-10-12 04:16 | 2009-10-12 04:45 | 2009-10-12 05:15
2009-10-12 03:16 | 60.004 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | 0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:16 | 2009-10-12 03:46 | 2009-10-12 04:16 | 2009-10-12 04:45 | 2009-10-12 05:15
2009-10-12 03:17 | 60.0025 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:46 | 2009-10-12 04:16 | 2009-10-12 04:45 | 2009-10-12 05:15
2009-10-12 03:17 | 60.001 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 1 | 1 | -0.001503 | 0.001503 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:46 | 2009-10-12 04:16 | 2009-10-12 04:45 | 2009-10-12 05:15
2009-10-12 03:17 | 59.999 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:46 | 2009-10-12 04:16 | 2009-10-12 04:45 | 2009-10-12 05:15
2009-10-12 03:17 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.0019989 | 0.0019989 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:46 | 2009-10-12 04:16 | 2009-10-12 04:45 | 2009-10-12 05:15
2009-10-12 03:17 | 59.9965 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00050354 | 0.00050354 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:46 | 2009-10-12 04:16 | 2009-10-12 04:46 | 2009-10-12 05:15
2009-10-12 03:17 | 59.996 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:46 | 2009-10-12 04:16 | 2009-10-12 04:46 | 2009-10-12 05:15
2009-10-12 03:17 | 59.9965 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:46 | 2009-10-12 04:16 | 2009-10-12 04:46 | 2009-10-12 05:15
2009-10-12 03:17 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00050354 | 0.00050354 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:46 | 2009-10-12 04:16 | 2009-10-12 04:46 | 2009-10-12 05:15
2009-10-12 03:17 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:46 | 2009-10-12 04:16 | 2009-10-12 04:46 | 2009-10-12 05:16
2009-10-12 03:17 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0 | 0 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:16 | 2009-10-12 04:46 | 2009-10-12 05:16
2009-10-12 03:17 | 59.998 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:16 | 2009-10-12 04:46 | 2009-10-12 05:16
2009-10-12 03:17 | 59.999 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:16 | 2009-10-12 04:46 | 2009-10-12 05:16
2009-10-12 03:17 | 59.9985 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:16 | 2009-10-12 04:46 | 2009-10-12 05:16
2009-10-12 03:17 | 59.998 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:46 | 2009-10-12 05:16
2009-10-12 03:17 | 59.9985 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:46 | 2009-10-12 05:16
2009-10-12 03:17 | 59.999 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:46 | 2009-10-12 05:16
2009-10-12 03:17 | 59.998 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:16
2009-10-12 03:17 | 59.997 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | -0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:16
2009-10-12 03:17 | 59.9985 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:17
2009-10-12 03:17 | 60 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  | -103 | 8094 | 1 | 0 | 1 | 0.0014992 | 0.0014992 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:17
2009-10-12 03:17 | 60.001 | 3724.9438 | 350 | [5 empty] | -103 | 8094 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:17
2009-10-12 03:17 | 60.002 | 3724.9438 | 350 | [5 empty] | -103 | 8094 | 1 | 1 | 1 | 0.00099945 | 0.00099945 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:17
2009-10-12 03:17 | 60.0015 | 3724.9438 | 350 | [5 empty] | -103 | 8094 | 1 | 1 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:17
2009-10-12 03:17 | 60.001 | 3724.9438 | 350 | [5 empty] | -103 | 8094 | 1 | 1 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:17
2009-10-12 03:17 | 60.0035 | 3724.9438 | 350 | [5 empty] | -103 | 8094 | 1 | 1 | 1 | 0.0025024 | 0.0025024 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:17
2009-10-12 03:17 | 60.006 | 3724.9438 | 350 | [5 empty] | -103 | 8094 | 1 | 1 | 1 | 0.0024986 | 0.0024986 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:17
2009-10-12 03:17 | 60.0055 | 3724.9438 | 350 | [5 empty] | -103 | 8094 | 1 | 1 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:17
2009-10-12 03:17 | 60.005 | 3724.9438 | 350 | [5 empty] | -103 | 8094 | 1 | 1 | 1 | -0.00049973 | 0.00049973 |  | 350 | -223.0157 | 16 |  |  |  | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:17 | 2009-10-12 04:47 | 2009-10-12 05:17
2009-10-12 03:17 | 59.9735 | -3775.9446 | 177.0459 | 0 | 3.2561 | 0 | 0 | 0 | -1538 | 114597.0938 | 1 | 0 | 1 | -0.031502 | 0.031502 | [7 empty] | 2009-10-12 03:17 | 2009-10-12 03:47 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:18
2009-10-12 03:17 | 59.973 | -3782.9004 | 177.0741 | 0 | 3.2566 | 0 | 0 | 0 | -1538 | 114608.4844 | 1 | 0 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:17 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:18
2009-10-12 03:18 | 59.9745 | -3766.98 | 177.1022 | 0 | 3.2571 | 0 | 0 | 0 | -1538 | 114589.8359 | 1 | 0 | 1 | 0.0014992 | 0.0014992 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:18
2009-10-12 03:18 | 59.9775 | -3771.0005 | 177.1304 | 0 | 3.2576 | 0 | 0 | 0 | -1538 | 114608.2422 | 1 | 0 | 1 | 0.0030022 | 0.0030022 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:18
2009-10-12 03:18 | 59.9795 | -3762.9497 | 177.1222 | 0 | 3.2581 | 0 | 0 | 0 | -1538 | 114599.4766 | 1 | 0 | 1 | 0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:18
2009-10-12 03:18 | 59.9815 | -3773.5837 | 177.114 | 0 | 3.2586 | 0 | 0 | 0 | -1538 | 114605.9766 | 1 | 0 | 1 | 0.0020027 | 0.0020027 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:18
2009-10-12 03:18 | 59.9835 | -3777.4119 | 177.1058 | 0 | 3.2591 | 0 | 0 | 0 | -1538 | 114612.4688 | 1 | 0 | 1 | 0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:18
2009-10-12 03:18 | 59.985 | -3779.3789 | 177.0976 | 0 | 3.2596 | 0 | 0 | 0 | -1538 | 114618.9688 | 1 | 0 | 1 | 0.0014992 | 0.0014992 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:18
2009-10-12 03:18 | 59.987 | -3780.0742 | 177.0895 | 0 | 3.2601 | 0 | 0 | 0 | -1538 | 114625.4609 | 1 | 0 | 1 | 0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:18
2009-10-12 03:18 | 59.988 | -3780.7698 | 177.0813 | 0 | 3.2606 | 0 | 0 | 0 | -1538 | 114631.9609 | 1 | 0 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:18
2009-10-12 03:18 | 59.989 | -3821.3293 | 177.0731 | 0 | 3.2611 | 0 | 0 | 0 | -1538 | 114681.5078 | 1 | 0 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:19
2009-10-12 03:18 | 59.9885 | -3811.4785 | 177.0649 | 0 | 3.2616 | 0 | 0 | 0 | -1538 | 114677.2344 | 1 | 0 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:48 | 2009-10-12 05:19
2009-10-12 03:18 | 59.9885 | -3811.4785 | 177.0567 | 0 | 3.2621 | 0 | 0 | 0 | -1538 | 114672.9531 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:49 | 2009-10-12 05:19
2009-10-12 03:18 | 59.9885 | -3826.2437 | 177.233 | 0 | 3.2626 | 0 | 0 | 0 | -1538 | 114697.6875 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:49 | 2009-10-12 05:19
2009-10-12 03:18 | 59.988 | -3796.3025 | 177.2432 | 0 | 3.2631 | 0 | 0 | 0 | -1538 | 114670.4531 | 1 | 0 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:18 | 2009-10-12 04:49 | 2009-10-12 05:19
2009-10-12 03:18 | 59.9875 | -3799.8381 | 177.2535 | 0 | 3.2636 | 0 | 0 | 0 | -1538 | 114669.375 | 1 | 0 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:19 | 2009-10-12 04:49 | 2009-10-12 05:19
2009-10-12 03:18 | 59.986 | -3787.8472 | 177.2637 | 0 | 3.2641 | 0 | 0 | 0 | -1538 | 114668.3047 | 1 | 0 | 1 | -0.0014992 | 0.0014992 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:19 | 2009-10-12 04:49 | 2009-10-12 05:19
2009-10-12 03:18 | 59.986 | -3765.8989 | 177.274 | 0 | 3.2646 | 0 | 0 | 0 | -1538 | 114644.1406 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:19 | 2009-10-12 04:49 | 2009-10-12 05:19
2009-10-12 03:18 | 59.985 | -3765.3997 | 177.574 | 0 | 3.2651 | 0 | 0 | 0 | -1538 | 114653.7031 | 1 | 0 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:19 | 2009-10-12 04:49 | 2009-10-12 05:19
2009-10-12 03:18 | 59.9855 | -3735.0667 | 177.5393 | 0 | 3.2656 | 0 | 0 | 0 | -1538 | 114634.8906 | 1 | 0 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:19 | 2009-10-12 04:49 | 2009-10-12 05:19
2009-10-12 03:18 | 59.986 | -3697.4478 | 177.5046 | 0 | 3.2661 | 0 | 0 | 0 | -1538 | 114616.0703 | 1 | 0 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:48 | 2009-10-12 04:19 | 2009-10-12 04:49 | 2009-10-12 05:20
2009-10-12 03:18 | 59.987 | -3691.5657 | 177.47 | 0 | 3.2666 | 0 | 0 | 0 | -1538 | 114613.2891 | 1 | 0 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:49 | 2009-10-12 04:19 | 2009-10-12 04:49 | 2009-10-12 05:20
2009-10-12 03:18 | 59.9875 | -3662.8027 | 177.4353 | 0 | 3.2671 | 0 | 0 | 0 | -1538 | 114587.1719 | 1 | 0 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:49 | 2009-10-12 04:19 | 2009-10-12 04:49 | 2009-10-12 05:20
2009-10-12 03:18 | 59.988 | -3690.9297 | 177.4007 | 0 | 3.2676 | 0 | 0 | 0 | -1538 | 114621.0234 | 1 | 0 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:49 | 2009-10-12 04:19 | 2009-10-12 04:49 | 2009-10-12 05:20
2009-10-12 03:18 | 59.989 | -3686.8179 | 177.4351 | 0 | 3.2681 | 0 | 0 | 0 | -1538 | 114627.1328 | 1 | 0 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:49 | 2009-10-12 04:19 | 2009-10-12 04:50 | 2009-10-12 05:20
2009-10-12 03:18 | 59.9885 | -3705.4702 | 177.4696 | 0 | 3.2686 | 0 | 0 | 0 | -1538 | 114633.2422 | 1 | 0 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:49 | 2009-10-12 04:19 | 2009-10-12 04:50 | 2009-10-12 05:20
2009-10-12 03:18 | 59.9875 | -3688.6106 | 177.5041 | 0 | 3.2691 | 0 | 0 | 0 | -1538 | 114639.3438 | 1 | 0 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:49 | 2009-10-12 04:19 | 2009-10-12 04:50 | 2009-10-12 05:20
2009-10-12 03:18 | 59.986 | -3691.4106 | 177.5386 | 0 | 3.2696 | 0 | 0 | 0 | -1538 | 114645.4531 | 1 | 0 | 1 | -0.0014992 | 0.0014992 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:49 | 2009-10-12 04:19 | 2009-10-12 04:50 | 2009-10-12 05:20
2009-10-12 03:18 | 59.9865 | -3667.6812 | 177.2966 | 0 | 3.2701 | 0 | 0 | 0 | -1538 | 114651.5625 | 1 | 0 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:49 | 2009-10-12 04:19 | 2009-10-12 04:50 | 2009-10-12 05:20
2009-10-12 03:18 | 59.9885 | -3675.2698 | 177.3262 | 0 | 3.2706 | 0 | 0 | 0 | -1538 | 114657.6719 | 1 | 0 | 1 | 0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:49 | 2009-10-12 04:19 | 2009-10-12 04:50 | 2009-10-12 05:20
2009-10-12 03:18 | 59.9885 | -3682.2891 | 177.3559 | 0 | 3.2711 | 0 | 0 | 0 | -1538 | 114667.1484 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:49 | 2009-10-12 04:20 | 2009-10-12 04:50 | 2009-10-12 05:21
2009-10-12 03:18 | 59.9895 | -3676.1567 | 177.3855 | 0 | 3.2716 | 0 | 0 | 0 | -1538 | 114676.6172 | 1 | 0 | 1 | 0.0010033 | 0.0010033 | [7 empty] | 2009-10-12 03:18 | 2009-10-12 03:49 | 2009-10-12 04:20 | 2009-10-12 04:50 | 2009-10-12 05:21
2009-10-12 03:19 | 59.9905 | -3685.3647 | 177.4151 | 0 | 3.2721 | 0 | 0 | 0 | -1538 | 114686.0938 | 1 | 0 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:49 | 2009-10-12 04:20 | 2009-10-12 04:50 | 2009-10-12 05:21
2009-10-12 03:19 | 59.9895 | -3688.4343 | 177.4448 | 0 | 3.2726 | 0 | 0 | 0 | -1538 | 114714.8281 | 1 | 0 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:49 | 2009-10-12 04:20 | 2009-10-12 04:50 | 2009-10-12 05:21
2009-10-12 03:19 | 59.989 | -3686.7036 | 177.4744 | 0 | 3.2731 | 0 | 0 | 0 | -1538 | 114709.2812 | 1 | 0 | 1 | -0.00050354 | 0.00050354 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:49 | 2009-10-12 04:20 | 2009-10-12 04:50 | 2009-10-12 05:21
2009-10-12 03:19 | 59.989 | -3666.8315 | 177.504 | 0 | 3.2736 | 0 | 0 | 0 | -1538 | 114703.7344 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:49 | 2009-10-12 04:20 | 2009-10-12 04:50 | 2009-10-12 05:21
2009-10-12 03:19 | 59.988 | -3658.208 | 177.5337 | 0 | 3.2741 | 0 | 0 | 0 | -1538 | 114698.1875 | 1 | 0 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:49 | 2009-10-12 04:20 | 2009-10-12 04:51 | 2009-10-12 05:21
2009-10-12 03:19 | 59.987 | -3660.3284 | 177.5633 | 0 | 3.2746 | 0 | 0 | 0 | -1538 | 114692.6406 | 1 | 0 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:49 | 2009-10-12 04:20 | 2009-10-12 04:51 | 2009-10-12 05:21
2009-10-12 03:19 | 59.9885 | -3650.3687 | 177.593 | 0 | 3.2751 | 0 | 0 | 0 | -1538 | 114701.3594 | 1 | 0 | 1 | 0.0014992 | 0.0014992 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:49 | 2009-10-12 04:20 | 2009-10-12 04:51 | 2009-10-12 05:21
2009-10-12 03:19 | 59.989 | -3676.9827 | 177.5519 | 0 | 3.2756 | 0 | 0 | 0 | -1538 | 114735.7969 | 1 | 0 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:49 | 2009-10-12 04:20 | 2009-10-12 04:51 | 2009-10-12 05:21
2009-10-12 03:19 | 59.9915 | -3685.1956 | 177.5109 | 0 | 3.2761 | 0 | 0 | 0 | -1538 | 114741.5859 | 1 | 0 | 1 | 0.0025024 | 0.0025024 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:49 | 2009-10-12 04:20 | 2009-10-12 04:51 | 2009-10-12 05:22
2009-10-12 03:19 | 59.9925 | -3686.6592 | 177.5109 | 0 | 3.2766 | 0 | 0 | 0 | -1538 | 114747.375 | 1 | 0 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:20 | 2009-10-12 04:51 | 2009-10-12 05:22
2009-10-12 03:19 | 59.9925 | -3686.6592 | 177.5109 | 0 | 3.2771 | 0 | 0 | 0 | -1538 | 114753.1641 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:20 | 2009-10-12 04:51 | 2009-10-12 05:22
2009-10-12 03:19 | 59.9935 | -3688.4341 | 177.1291 | 0 | 3.2776 | 0 | 0 | 0 | -1538 | 114758.9531 | 1 | 0 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:20 | 2009-10-12 04:51 | 2009-10-12 05:22
2009-10-12 03:19 | 59.995 | -3671.9128 | 177.1357 | 0 | 3.2781 | 0 | 0 | 0 | -1538 | 114757.25 | 1 | 0 | 1 | 0.0014992 | 0.0014992 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:20 | 2009-10-12 04:51 | 2009-10-12 05:22
2009-10-12 03:19 | 59.9955 | -3679.8362 | 177.1423 | 0 | 3.2786 | 0 | 0 | 0 | -1538 | 114755.5547 | 1 | 0 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:51 | 2009-10-12 05:22
2009-10-12 03:19 | 59.997 | -3690.4285 | 177.1488 | 0 | 3.2791 | 0 | 0 | 0 | -1538 | 114761.2969 | 1 | 0 | 1 | 0.001503 | 0.001503 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:51 | 2009-10-12 05:22
2009-10-12 03:19 | 59.999 | -3685.7803 | 177.1554 | 0 | 3.2796 | 0 | 0 | 0 | -1538 | 114767.0469 | 1 | 0 | 1 | 0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:51 | 2009-10-12 05:22
2009-10-12 03:19 | 59.9995 | -3645.4561 | 176.9818 | 0 | 3.2801 | 0 | 0 | 0 | -1538 | 114737.8594 | 1 | 0 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:22
2009-10-12 03:19 | 59.9995 | -3674.9514 | 176.9808 | 0 | 3.2806 | 0 | 0 | 0 | -1538 | 114768.2812 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:22
2009-10-12 03:19 | 60.0015 | -3657.6091 | 176.9799 | 0 | 3.2811 | 0 | 0 | 0 | -1538 | 114749.8516 | 1 | 1 | 1 | 0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:23
2009-10-12 03:19 | 60.004 | -3652.4097 | 176.9789 | 0 | 3.2816 | 0 | 0 | 0 | -1538 | 114755.7188 | 1 | 1 | 1 | 0.0024986 | 0.0024986 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:23
2009-10-12 03:19 | 60.0065 | -3662.9346 | 176.9779 | 0 | 3.2821 | 0 | 0 | 0 | -1538 | 114761.5938 | 1 | 1 | 1 | 0.0025024 | 0.0025024 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:23
2009-10-12 03:19 | 60.007 | -3657.0049 | 176.9093 | 0 | 3.2826 | 0 | 0 | 0 | -1538 | 114767.4609 | 1 | 1 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:23
2009-10-12 03:19 | 60.006 | -3668.9353 | 176.8408 | 0 | 3.2831 | 0 | 0 | 0 | -1538 | 114773.3359 | 1 | 1 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:23
2009-10-12 03:19 | 60.007 | -3671.2014 | 176.8898 | 0 | 3.2836 | 0 | 0 | 0 | -1538 | 114779.2031 | 1 | 1 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:23
2009-10-12 03:19 | 60.0095 | -3678.488 | 176.9389 | 0 | 3.2841 | 0 | 0 | 0 | -1538 | 114777.3984 | 1 | 1 | 1 | 0.0024986 | 0.0024986 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:23
2009-10-12 03:19 | 60.009 | -3675.2192 | 176.988 | 0 | 3.2846 | 0 | 0 | 0 | -1538 | 114775.5938 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:23
2009-10-12 03:19 | 60.0105 | -3690.9167 | 178.1741 | 0 | 3.2851 | 0 | 0 | 0 | -1538 | 114797.1641 | 1 | 1 | 1 | 0.0014992 | 0.0014992 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:23
2009-10-12 03:19 | 60.01 | -3678.5527 | 178.2445 | 0 | 3.2856 | 0 | 0 | 0 | -1538 | 114781.2734 | 1 | 1 | 1 | -0.00049591 | 0.00049591 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:21 | 2009-10-12 04:52 | 2009-10-12 05:23
2009-10-12 03:19 | 60.0105 | -3692.1218 | 178.0686 | 0 | 3.286 | 0 | 0 | 0 | -1538 | 114796.3438 | 1 | 1 | 1 | 0.00049591 | 0.00049591 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:50 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:24
2009-10-12 03:19 | 60.0105 | -3699.7207 | 178.0559 | 0 | 3.2865 | 0 | 0 | 0 | -1538 | 114811.4219 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:19 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:24
2009-10-12 03:20 | 60.0105 | -3686.4448 | 178.0433 | 0 | 3.287 | 0 | 0 | 0 | -1538 | 114804.9453 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:24
2009-10-12 03:20 | 60.01 | -3655.8389 | 177.9381 | 0 | 3.2875 | 0 | 0 | 0 | -1538 | 114798.4688 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:24
2009-10-12 03:20 | 60.01 | -3646 | 177.833 | 0 | 3.288 | 0 | 0 | 0 | -1538 | 114791.9922 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:24
2009-10-12 03:20 | 60.01 | -3639.0452 | 177.7278 | 0 | 3.2885 | 0 | 0 | 0 | -1538 | 114785.5156 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:24
2009-10-12 03:20 | 60.01 | -3603.6243 | 177.6902 | 0 | 3.289 | 0 | 0 | 0 | -1538 | 114747.1094 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:24
2009-10-12 03:20 | 60.01 | -3614.6194 | 177.6525 | 0 | 3.2895 | 0 | 0 | 0 | -1538 | 114753.8125 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:24
2009-10-12 03:20 | 60.013 | -3621.405 | 177.3792 | 0 | 3.29 | 0 | 0 | 0 | -1538 | 114789.0234 | 1 | 1 | 1 | 0.0030022 | 0.0030022 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:24
2009-10-12 03:20 | 60.011 | -3626.6216 | 177.4224 | 0 | 3.2905 | 0 | 0 | 0 | -1538 | 114788.2656 | 1 | 1 | 1 | -0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:24
2009-10-12 03:20 | 60.011 | -3614.8538 | 177.4656 | 0 | 3.291 | 0 | 0 | 0 | -1538 | 114787.5 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:25
2009-10-12 03:20 | 60.012 | -3618.2603 | 177.5088 | 0 | 3.2915 | 0 | 0 | 0 | -1538 | 114786.7344 | 1 | 1 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:53 | 2009-10-12 05:25
2009-10-12 03:20 | 60.012 | -3618.2603 | 177.552 | 0 | 3.292 | 0 | 0 | 0 | -1538 | 114785.9766 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:54 | 2009-10-12 05:25
2009-10-12 03:20 | 60.0135 | -3639.2646 | 177.332 | 0 | 3.2925 | 0 | 0 | 0 | -1538 | 114829.2891 | 1 | 1 | 1 | 0.0014992 | 0.0014992 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:54 | 2009-10-12 05:25
2009-10-12 03:20 | 60.0145 | -3630.0784 | 177.112 | 0 | 3.293 | 0 | 0 | 0 | -1538 | 114827.0547 | 1 | 1 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:22 | 2009-10-12 04:54 | 2009-10-12 05:25
2009-10-12 03:20 | 60.014 | -3622.9695 | 177.112 | 0 | 3.2935 | 0 | 0 | 0 | -1538 | 114824.8203 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:23 | 2009-10-12 04:54 | 2009-10-12 05:25
2009-10-12 03:20 | 60.0135 | -3617.3093 | 177.112 | 0 | 3.294 | 0 | 0 | 0 | -1538 | 114822.5859 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:23 | 2009-10-12 04:54 | 2009-10-12 05:25
2009-10-12 03:20 | 60.0145 | -3638.8044 | 177.112 | 0 | 3.2945 | 0 | 0 | 0 | -1538 | 114837.3828 | 1 | 1 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:23 | 2009-10-12 04:54 | 2009-10-12 05:25
2009-10-12 03:20 | 60.0145 | -3616.427 | 177.4333 | 0 | 3.295 | 0 | 0 | 0 | -1538 | 114821.2344 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:23 | 2009-10-12 04:54 | 2009-10-12 05:25
2009-10-12 03:20 | 60.0135 | -3644.9475 | 177.4306 | 0 | 3.2955 | 0 | 0 | 0 | -1538 | 114858.8828 | 1 | 1 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:23 | 2009-10-12 04:54 | 2009-10-12 05:25
2009-10-12 03:20 | 60.0145 | -3614.48 | 177.4278 | 0 | 3.296 | 0 | 0 | 0 | -1538 | 114834.8125 | 1 | 1 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:51 | 2009-10-12 04:23 | 2009-10-12 04:54 | 2009-10-12 05:26
2009-10-12 03:20 | 60.015 | -3626.4053 | 177.425 | 0 | 3.2965 | 0 | 0 | 0 | -1538 | 114851.4531 | 1 | 1 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:52 | 2009-10-12 04:23 | 2009-10-12 04:54 | 2009-10-12 05:26
2009-10-12 03:20 | 60.015 | -3598.1575 | 177.4222 | 0 | 3.297 | 0 | 0 | 0 | -1538 | 114819.5234 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:52 | 2009-10-12 04:23 | 2009-10-12 04:54 | 2009-10-12 05:26
2009-10-12 03:20 | 60.0175 | -3602.1685 | 177.4194 | 0 | 3.2975 | 0 | 0 | 0 | -1538 | 114832.4141 | 1 | 1 | 1 | 0.0025024 | 0.0025024 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:52 | 2009-10-12 04:23 | 2009-10-12 04:54 | 2009-10-12 05:26
2009-10-12 03:20 | 60.018 | -3633.563 | 177.4167 | 0 | 3.298 | 0 | 0 | 0 | -1538 | 114872.4141 | 1 | 1 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:52 | 2009-10-12 04:23 | 2009-10-12 04:55 | 2009-10-12 05:26
2009-10-12 03:20 | 60.019 | -3609.3499 | 177.4139 | 0 | 3.2985 | 0 | 0 | 0 | -1538 | 114853.0391 | 1 | 1 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:52 | 2009-10-12 04:23 | 2009-10-12 04:55 | 2009-10-12 05:26
2009-10-12 03:20 | 60.0185 | -3594.4536 | 177.4111 | 0 | 3.299 | 0 | 0 | 0 | -1538 | 114848.2656 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:52 | 2009-10-12 04:23 | 2009-10-12 04:55 | 2009-10-12 05:26
2009-10-12 03:20 | 60.017 | -3584.6199 | 177.4083 | 0 | 3.2995 | 0 | 0 | 0 | -1538 | 114843.5 | 1 | 1 | 1 | -0.001503 | 0.001503 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:52 | 2009-10-12 04:23 | 2009-10-12 04:55 | 2009-10-12 05:26
2009-10-12 03:20 | 60.017 | -3602.0625 | 177.9958 | 0 | 3.3 | 0 | 0 | 0 | -1538 | 114873.3828 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:52 | 2009-10-12 04:23 | 2009-10-12 04:55 | 2009-10-12 05:26
2009-10-12 03:20 | 60.016 | -3597.5964 | 178.0279 | 0 | 3.3005 | 0 | 0 | 0 | -1538 | 114869.7344 | 1 | 1 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:52 | 2009-10-12 04:23 | 2009-10-12 04:55 | 2009-10-12 05:26
2009-10-12 03:20 | 60.0155 | -3591.4363 | 178.06 | 0 | 3.301 | 0 | 0 | 0 | -1538 | 114866.0859 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:52 | 2009-10-12 04:24 | 2009-10-12 04:55 | 2009-10-12 05:27
2009-10-12 03:20 | 60.0155 | -3597.8816 | 178.092 | 0 | 3.3015 | 0 | 0 | 0 | -1538 | 114887.3359 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:20 | 2009-10-12 03:52 | 2009-10-12 04:24 | 2009-10-12 04:55 | 2009-10-12 05:27
2009-10-12 03:21 | 60.015 | -3627.9463 | 178.1241 | 0 | 3.302 | 0 | 0 | 0 | -1538 | 114908.5781 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:52 | 2009-10-12 04:24 | 2009-10-12 04:55 | 2009-10-12 05:27
2009-10-12 03:21 | 60.0145 | -3639.3708 | 178.1561 | 0 | 3.3025 | 0 | 0 | 0 | -1538 | 114929.8281 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:52 | 2009-10-12 04:24 | 2009-10-12 04:55 | 2009-10-12 05:27
2009-10-12 03:21 | 60.014 | -3654.1187 | 178.1882 | 0 | 3.303 | 0 | 0 | 0 | -1538 | 114951.0781 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:52 | 2009-10-12 04:24 | 2009-10-12 04:55 | 2009-10-12 05:27
2009-10-12 03:21 | 60.014 | -3633.5557 | 178.2203 | 0 | 3.3035 | 0 | 0 | 0 | -1538 | 114934 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:52 | 2009-10-12 04:24 | 2009-10-12 04:55 | 2009-10-12 05:27
2009-10-12 03:21 | 60.0125 | -3618.165 | 178.2203 | 0 | 3.304 | 0 | 0 | 0 | -1538 | 114916.9219 | 1 | 1 | 1 | -0.0014992 | 0.0014992 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:52 | 2009-10-12 04:24 | 2009-10-12 04:56 | 2009-10-12 05:27
2009-10-12 03:21 | 60.012 | -3634.3833 | 178.2203 | 0 | 3.3045 | 0 | 0 | 0 | -1538 | 114935.1875 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:52 | 2009-10-12 04:24 | 2009-10-12 04:56 | 2009-10-12 05:27
2009-10-12 03:21 | 60.011 | -3634.625 | 178.004 | 0 | 3.305 | 0 | 0 | 0 | -1538 | 114953.4609 | 1 | 1 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:52 | 2009-10-12 04:24 | 2009-10-12 04:56 | 2009-10-12 05:27
2009-10-12 03:21 | 60.0095 | -3656.3638 | 177.9894 | 0 | 3.3056 | 0 | 0 | 0 | -1538 | 114971.7266 | 1 | 1 | 1 | -0.001503 | 0.001503 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:52 | 2009-10-12 04:24 | 2009-10-12 04:56 | 2009-10-12 05:27
2009-10-12 03:21 | 60.009 | -3652.4385 | 177.9747 | 0 | 3.3062 | 0 | 0 | 0 | -1538 | 114969.125 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:52 | 2009-10-12 04:24 | 2009-10-12 04:56 | 2009-10-12 05:28
2009-10-12 03:21 | 60.008 | -3649.4253 | 177.9601 | 0 | 3.3067 | 0 | 0 | 0 | -1538 | 114966.5234 | 1 | 1 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:24 | 2009-10-12 04:56 | 2009-10-12 05:28
2009-10-12 03:21 | 60.008 | -3649.4253 | 177.9454 | 0 | 3.3073 | 0 | 0 | 0 | -1538 | 114963.9219 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:24 | 2009-10-12 04:56 | 2009-10-12 05:28
2009-10-12 03:21 | 60.005 | -3647.1274 | 177.6161 | 0 | 3.3078 | 0 | 0 | 0 | -1538 | 114992.4141 | 1 | 1 | 1 | -0.0029984 | 0.0029984 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:24 | 2009-10-12 04:56 | 2009-10-12 05:28
2009-10-12 03:21 | 60.0045 | -3599.375 | 177.7919 | 0 | 3.3084 | 0 | 0 | 0 | -1538 | 114955.5156 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:24 | 2009-10-12 04:56 | 2009-10-12 05:28
2009-10-12 03:21 | 60.003 | -3595.9888 | 177.9678 | 0 | 3.3089 | 0 | 0 | 0 | -1538 | 114953.2031 | 1 | 1 | 1 | -0.001503 | 0.001503 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:56 | 2009-10-12 05:28
2009-10-12 03:21 | 60.0025 | -3581.751 | 177.972 | 0 | 3.3095 | 0 | 0 | 0 | -1538 | 114936.6094 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:56 | 2009-10-12 05:28
2009-10-12 03:21 | 60.003 | -3579.2229 | 177.9762 | 0 | 3.31 | 0 | 0 | 0 | -1538 | 114920.0156 | 1 | 1 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:56 | 2009-10-12 05:28
2009-10-12 03:21 | 60.003 | -3545.5803 | 177.9805 | 0 | 3.3106 | 0 | 0 | 0 | -1538 | 114903.4219 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:28
2009-10-12 03:21 | 60.002 | -3543.6055 | 177.9847 | 0 | 3.3112 | 0 | 0 | 0 | -1538 | 114920.9844 | 1 | 1 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:28
2009-10-12 03:21 | 60.003 | -3523.4175 | 177.8142 | 0 | 3.3117 | 0 | 0 | 0 | -1538 | 114913.9766 | 1 | 1 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:29
2009-10-12 03:21 | 60.003 | -3523.4175 | 177.8515 | 0 | 3.3123 | 0 | 0 | 0 | -1538 | 114906.9688 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:29
2009-10-12 03:21 | 60.003 | -3525.0737 | 177.8888 | 0 | 3.3128 | 0 | 0 | 0 | -1538 | 114899.9609 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:29
2009-10-12 03:21 | 60.0035 | -3527.5989 | 177.9261 | 0 | 3.3134 | 0 | 0 | 0 | -1538 | 114913.0547 | 1 | 1 | 1 | 0.00050354 | 0.00050354 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:29
2009-10-12 03:21 | 60.0005 | -3539.3201 | 177.9633 | 0 | 3.3139 | 0 | 0 | 0 | -1538 | 114926.1484 | 1 | 1 | 1 | -0.0030022 | 0.0030022 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:29
2009-10-12 03:21 | 59.9985 | -3546.1863 | 178.0006 | 0 | 3.3145 | 0 | 0 | 0 | -1538 | 114939.2422 | 1 | 0 | 1 | -0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:29
2009-10-12 03:21 | 59.9985 | -3546.5027 | 178.0379 | 0 | 3.315 | 0 | 0 | 0 | -1538 | 114940.4141 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:29
2009-10-12 03:21 | 59.9985 | -3549.6531 | 178.0752 | 0 | 3.3156 | 0 | 0 | 0 | -1538 | 114941.5859 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:29
2009-10-12 03:21 | 59.9955 | -3563.5154 | 178.1125 | 0 | 3.3162 | 0 | 0 | 0 | -1538 | 114978.4453 | 1 | 0 | 1 | -0.0030022 | 0.0030022 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:29
2009-10-12 03:21 | 59.9975 | -3571.4043 | 178.1498 | 0 | 3.3167 | 0 | 0 | 0 | -1538 | 114986.6797 | 1 | 0 | 1 | 0.0020027 | 0.0020027 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:25 | 2009-10-12 04:57 | 2009-10-12 05:29
2009-10-12 03:21 | 59.9975 | -3601.187 | 178.1871 | 0 | 3.3173 | 0 | 0 | 0 | -1538 | 115028.4766 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:53 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:30
2009-10-12 03:21 | 59.998 | -3597.5066 | 178.1904 | 0 | 3.3178 | 0 | 0 | 0 | -1538 | 115018.625 | 1 | 0 | 1 | 0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:21 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:30
2009-10-12 03:22 | 60 | -3582.113 | 178.1937 | 0 | 3.3184 | 0 | 0 | 0 | -1538 | 115008.7734 | 1 | 0 | 1 | 0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:30
2009-10-12 03:22 | 60.002 | -3585.3484 | 178.1971 | 0 | 3.3189 | 0 | 0 | 0 | -1538 | 115022.9688 | 1 | 1 | 1 | 0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:30
2009-10-12 03:22 | 60.0015 | -3598.5596 | 178.0494 | 0 | 3.3195 | 0 | 0 | 0 | -1538 | 115037.1641 | 1 | 1 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:30
2009-10-12 03:22 | 60.0005 | -3597.6201 | 178.0409 | 0 | 3.32 | 0 | 0 | 0 | -1538 | 115032.6875 | 1 | 1 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:30
2009-10-12 03:22 | 60.0005 | -3570.707 | 178.0324 | 0 | 3.3206 | 0 | 0 | 0 | -1538 | 115004.8203 | 1 | 1 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:30
2009-10-12 03:22 | 59.9985 | -3584.6472 | 178.0239 | 0 | 3.3212 | 0 | 0 | 0 | -1538 | 115034 | 1 | 0 | 1 | -0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:30
2009-10-12 03:22 | 59.9985 | -3596.7856 | 178.0154 | 0 | 3.3217 | 0 | 0 | 0 | -1538 | 115063.1719 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:30
2009-10-12 03:22 | 59.9995 | -3601.6428 | 178.1285 | 0 | 3.3223 | 0 | 0 | 0 | -1538 | 115057.9688 | 1 | 0 | 1 | 0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:30
2009-10-12 03:22 | 59.9995 | -3616.6118 | 178.2417 | 0 | 3.3228 | 0 | 0 | 0 | -1538 | 115077.8984 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:31
2009-10-12 03:22 | 59.9995 | -3624.1108 | 178.2332 | 0 | 3.3234 | 0 | 0 | 0 | -1538 | 115083.5547 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:58 | 2009-10-12 05:31
2009-10-12 03:22 | 59.9995 | -3624.1108 | 178.2247 | 0 | 3.3239 | 0 | 0 | 0 | -1538 | 115089.2109 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:59 | 2009-10-12 05:31
2009-10-12 03:22 | 59.9995 | -3638.1519 | 178.2163 | 0 | 3.3245 | 0 | 0 | 0 | -1538 | 115094.8594 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:59 | 2009-10-12 05:31
2009-10-12 03:22 | 59.9985 | -3646.4802 | 178.0721 | 0 | 3.325 | 0 | 0 | 0 | -1538 | 115100.5156 | 1 | 0 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:26 | 2009-10-12 04:59 | 2009-10-12 05:31
2009-10-12 03:22 | 59.997 | -3654.4309 | 177.9278 | 0 | 3.3256 | 0 | 0 | 0 | -1538 | 115106.1719 | 1 | 0 | 1 | -0.0014992 | 0.0014992 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:27 | 2009-10-12 04:59 | 2009-10-12 05:31
2009-10-12 03:22 | 59.9955 | -3641.5295 | 177.9405 | 0 | 3.3262 | 0 | 0 | 0 | -1538 | 115095.0391 | 1 | 0 | 1 | -0.001503 | 0.001503 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:27 | 2009-10-12 04:59 | 2009-10-12 05:31
2009-10-12 03:22 | 59.9935 | -3660.6372 | 177.9532 | 0 | 3.3267 | 0 | 0 | 0 | -1538 | 115115.3281 | 1 | 0 | 1 | -0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:27 | 2009-10-12 04:59 | 2009-10-12 05:31
2009-10-12 03:22 | 59.9935 | -3642.5996 | 178.4532 | 0 | 3.3273 | 0 | 0 | 0 | -1538 | 115103.2891 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:27 | 2009-10-12 04:59 | 2009-10-12 05:31
2009-10-12 03:22 | 59.9915 | -3658.0085 | 178.4307 | 0 | 3.3278 | 0 | 0 | 0 | -1538 | 115124.7109 | 1 | 0 | 1 | -0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:27 | 2009-10-12 04:59 | 2009-10-12 05:31
2009-10-12 03:22 | 59.9905 | -3635.1265 | 178.4082 | 0 | 3.3284 | 0 | 0 | 0 | -1538 | 115102.3359 | 1 | 0 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:54 | 2009-10-12 04:27 | 2009-10-12 04:59 | 2009-10-12 05:32
2009-10-12 03:22 | 59.9905 | -3632.7544 | 178.3857 | 0 | 3.3289 | 0 | 0 | 0 | -1538 | 115103.5781 | 1 | 0 | 1 | 0 | 0 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:55 | 2009-10-12 04:27 | 2009-10-12 04:59 | 2009-10-12 05:32
2009-10-12 03:22 | 59.9895 | -3587.5295 | 178.3633 | 0 | 3.3295 | 0 | 0 | 0 | -1538 | 115055.4609 | 1 | 0 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:55 | 2009-10-12 04:27 | 2009-10-12 04:59 | 2009-10-12 05:32
2009-10-12 03:22 | 59.9885 | -3581.3916 | 178.3408 | 0 | 3.33 | 0 | 0 | 0 | -1538 | 115076.4062 | 1 | 0 | 1 | -0.0010033 | 0.0010033 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:55 | 2009-10-12 04:27 | 2009-10-12 04:59 | 2009-10-12 05:32
2009-10-12 03:22 | 59.9865 | -3570.4934 | 178.3183 | 0 | 3.3306 | 0 | 0 | 0 | -1538 | 115069.4844 | 1 | 0 | 1 | -0.0019989 | 0.0019989 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:55 | 2009-10-12 04:27 | 2009-10-12 05:00 | 2009-10-12 05:32
2009-10-12 03:22 | 59.986 | -3559.8613 | 178.2958 | 0 | 3.3311 | 0 | 0 | 0 | -1538 | 115062.5547 | 1 | 0 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:55 | 2009-10-12 04:27 | 2009-10-12 05:00 | 2009-10-12 05:32
2009-10-12 03:22 | 59.985 | -3555.6108 | 178.2733 | 0 | 3.3317 | 0 | 0 | 0 | -1538 | 115055.625 | 1 | 0 | 1 | -0.00099945 | 0.00099945 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:55 | 2009-10-12 04:27 | 2009-10-12 05:00 | 2009-10-12 05:32
2009-10-12 03:22 | 59.9845 | -3554.1855 | 178.2508 | 0 | 3.3323 | 0 | 0 | 0 | -1538 | 115048.7031 | 1 | 0 | 1 | -0.00049973 | 0.00049973 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:55 | 2009-10-12 04:27 | 2009-10-12 05:00 | 2009-10-12 05:32
2009-10-12 03:22 | 59.9825 | -3570.8345 | 178.2283 | 0 | 3.3328 | 0 | 0 | 0 | -1538 | 115077.3438 | 1 | 0 | 1 | -0.0020027 | 0.0020027 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:55 | 2009-10-12 04:27 | 2009-10-12 05:00 | 2009-10-12 05:32
2009-10-12 03:22 | 59.981 | -3590.7007 | 178.158 | 0 | 3.3334 | 0 | 0 | 0 | -1538 | 115105.9844 | 1 | 0 | 1 | -0.0014992 | 0.0014992 | [7 empty] | 2009-10-12 03:22 | 2009-10-12 03:55 | 2009-10-12 04:27 | 2009-10-12 05:00 | 2009-10-12 05:32

## Copy Results
Balancing Authority Name: | MyBA |  | MyBA_091012_0227_FRS_Form2.9a.xlsm
| Interconnection Prevailing UFLS First Step Relay trip point | 59.5 | Hz |  | (Suggested file name)
| Interconnection High Relay trip point | 60.5 | Hz
Special Instructions for HISTORIAN non-standard Excel Date/Time format! | Do not copy your date/time information into column A of the "Data" worksheet. Instead, enter the beginning Date/Time of your data into cell "A2" in the "Data" Worksheet (using the format provided). Then select your AGC scan rate in cell "B2". (2 sec, 3 sec, 4 sec, 5 sec or 6 sec). Note, a data value must exist for each AGC scan. The spreadsheet will fill the Date/Time column with the correct times and format.
Note: See "Instruction" tab for more detailed instructions. |  |  |  | Auto | Event Detection | Auto
|  |  | 40098.1024 | 1245 | Manually selected row number of the Event Starting Time. | Manual
Step 1. | Copy and Paste Event Data into the appropriate cells of the "Data" worksheet. |  | 40098.1062 | 1442 | Manually selected row number of the Event Ending Time.
Maintain date and time format of mm/dd/yy hh:mm:ss.
Step 2. | Data must start at least 2 full minutes before the beginning of the event. | 40098.1024
Collect the same amount of data for each event. Suggest 2 to 3 minutes before to 15 minutes after (up to 60 minutes total). Delete unused rows of data in the Data worksheet below your data, columns A through R. You must also delete any un-used event detection formulas in columns M through R as well.
Step 3. | Enter your BA name in cell B1 of this worksheet.
Step 4. | Verify that the "Auto" Event Detection selected the correct event. Verify time and delta Hz | 40098.1062
by comparing time of event and delta Hz on graph to the right to that on Form 1 for this event. If the wrong event was selected, in cell "E4" of this worksheet select "Manual" and manually select the beginning and ending row numbers of the desired event and enter these in cells "E5" and "E6". Only rarely should you have to use the "Manual" process.
Step 5. | Verify that the "Auto" selection of T(0) is correct by observing "Graph 20 to 52s".
The very first frequency data point of the event on the graph
must not be included in the "A Value" average. This is accomplished when the
first frequency data point of the event is dead center of the graph on the center
vertical grid line. The Auto event detection will select the single largest event in the
data provided. An adjustment for T(0) alignment is provided in Cell Q3 on the Graph 20 to 52s.
Step 6. | When T(0) is properly aligned. Hit the big blue button to copy your data for pasting into FRS Form 1 "BA Event Data" worksheet.
Step 7. | Paste data into "FRS Form 1" in the appropriate row on the "BA Event Data" worksheet.
Be sure to use the latest version of Form 1. This is Form 2.9a so use Form 1.9.
Step 8. | Save this workbook using the following file name in bold below:
| 2009-10-12 02:27 | Date yymmdd
| 40098.1024 | Time hh:ss of T(0)
Where "MyBA" = your BA mnemonic
MyBA_091012_0227_FRS_Form2.9a.xlsm
Note on E8: With Auto selected the spreadsheet will find the highest frequency change in the frequency data. On rare occasions this is not the event that you want to evaluate. By selecting manual you can enter the starting and ending event "row" numbers from the "Data" worksheet. The spreadsheet will then evaluate PFR using these manually entered start and end times.
Copy Form 2 data for Pasting into Form 1

## Evaluation
| 2 | seconds |  |  | Date: | 2009-10-12 02:27 |  |  | Balancing Authority | MyBA | [5 empty] | A Point | 40098.1023 | [5 empty] | Non-Conforming Load sign convention | - | (If Data is positive for Load then enter "+" else "-") | [11 empty] | Date: | 2009-10-12 02:27 |  |  |  | Frequency Response Initiative - Additional Primary Frequency Response Evaluation Points
[5 empty] | Time of T(0) | 40098.1024 |  |  | Grid Nominal Frequency | 60 | Hz |  |  |  |  | FPointA | 60.041 | 40098.1023 | [18 empty] | Time of T(0) | 40098.1024 |  |  |  | Frequency @ T(+46) | 59.89 | Hz
[5 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [9 empty] | A Value | 60.0421 | [19 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 |  |  |  | Frequency @ T(+76) | 59.863 | Hz | Actual |  | JOU | Non- |  | Transferred | Contingent
[5 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0421 | Hz |  | Droop Setting | 5% | 3 | Hz |  |  |  | C Value | 59.836 | [19 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0421 | Hz |  |  | Frequency @ T(+106) | 59.899 | Hz | Primary | Un-adjusted | Dynamic | Conforming | Pumped | Frequency | BA | Adjusted
[5 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8891 | Hz |  | Dead band Setting | 0 | Hz |  |  |  |  | Delta FC | [20 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8891 | Hz |  |  | Frequency @ T(+136) | 59.92 | Hz | Freq Response | P.U. | Schedules | Load | Hydro | Response | Lost Generation | P.U.
[5 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15301 | Hz |  | Hz Span | 3 | Hz | [25 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15301 | Hz |  |  | Frequency @ T(+166) | 59.937 | Hz | MW | Performance | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Performance
[5 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3647.0624 | MW | [29 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3647.0624 | MW |  |  | EPFR @ T(+46) | 113.3006 | MW | 172.1449 | 1.5194 | -15 | -51.903 | 16 | 15.2126 | -15 | 1.5696
[5 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 3788.3545 | MW | [29 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] adj for contingency loss | 3803.3545 | MW |  |  | EPFR @ T(+76) | 141.1111 | MW | 196.0438 | 1.3893 | -15 | -59.5417 | 16 | 17.9126 | -15 | 1.4646
[5 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 156.2921 | MW | [29 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 156.2921 | MW |  |  | EPFR @ T(+106) | 104.0318 | MW | 178.1717 | 1.7127 | -15 | -63.3218 | 16 | 14.3127 | -15 | 1.8858
[5 empty] | Initial Performance Ramp Magnitude Adjustment | -12.6113 | MW | [34 empty] | EPFR @ T(+136) | 82.4019 | MW | 143.1241 | 1.7369 | -15 | -54.4992 | 16 | 12.2127 | -15 | 1.8739
[5 empty] | EPFR Pre-Perturbation Average | -43.389 | MW | [29 empty] | EPFR Pre-Perturbation Average | -43.389 | MW |  |  | EPFR @ T(+166) | 64.8897 | MW | 133.6248 | 2.0593 | -15 | -63.7575 | 16 | 10.5125 | -15 | 2.4021
[5 empty] | EPFR Post-Perturbation Average | 114.2087 | MW | [29 empty] | EPFR Post-Perturbation Average | 114.2087 | MW
[5 empty] | EPFR Delta | 157.5977 | MW |  | TC (frequency response filter constant) | 0.35 | Time Constant for delayed delivery of PFR during Sustained Measure | [25 empty] | EPFR Unadjusted | 157.5977 | MW
[37 empty] | EPFR Adjusted | 149.9241 | MW |  |  | T(20) to T(52) Evaluation
[37 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | Low Hz | Delta Hz Event | [26 empty] | Pre Non-Conforming Load MW | -165.4764 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | 3764.0997 | Actual Interchange MW Average during frequency recovery period | [26 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.389 | MW
[9 empty] | 3785.8759 | Target Interchange MW Average during frequency recovery period | [31 empty] | EPFR for Bias Setting Post-Perturbation Average | 114.2087 | MW
|  |  | EPFR = Expected Primary Frequency Response |  | EPFR(Final) | 144.9865 | MW |  | 3722.1754 | Interchange Average Ramp MW during frequency recovery period | [26 empty] | Pre Transferred Frequency Response MW | -4.2125 | MW |  |  | EPFR for Bias Setting Delta | 157.5977 | MW
[5 empty] | MW Response in right direction for frequency delta | Yes |  |  | 3645.4458 | Actual MW @ T(-4) | [26 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery % of Bias | 99.17%
[9 empty] | 97.8275 | Starting and Ending Difference in Interchange MW during frequency recovery period (indicates ramp direction during recovery period) | [26 empty] | Sum of Pre Perturbation Adjustments | 180.3111 | MW
[9 empty] | 0:06 | Event Duration (h:mm:ss)
[9 empty] | No | Target MW Average minus MW @ T(-4) less than zero | [26 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7650.975 | MW
[9 empty] | 140.4301 | Interchange Target Relative Average Change - MW (Low Frequency Event) | [26 empty] | Post Non-Conforming Load MW | -216.2155 | MW |  |  | Post-Perturbation BA Load | 7632 | MW
[9 empty] | 118.6539 | Interchange Actual Relative Average Change - MW (Low Frequency Event) | [26 empty] | Post Pumped Hydro MW | 12.7647 | MW |  |  | Pre to Post Perturbation BA Load Change | -18.975 | MW
[9 empty] | No | Interchange Actual Average minus MW @ T(-4) less than zero | [31 empty] | Load Dampening Frequency Response | -12.4014 | MW/0.1 Hz
[9 empty] | Yes | Interchange Average MW minus MW @ T(-4) greater than zero | [26 empty] | Post Transferred Frequency Response MW | 11.0882 | MW |  |  | Load Dampening % of Total BA Frequency Response | 12.14%
[9 empty] | Yes | Interchange Target MW Average minus MW @ T(-4) greater than zero | [26 empty] | Post Contingent BA Lost Generation MW | 0 | MW
[9 empty] | 42.6026 | Interchange Target Relative Average Change - MW (High Frequency Event) | [26 empty] | Sum of Post Perturbation Adjustments | 142.6375 | MW
[9 empty] | 20.8264 | Interchange Actual Relative Average Change - MW (High Frequency Event) | [26 empty] | Net Total Adjustments MW | -7.6736 | MW |  |  | Average Bias Setting when Hz is greater than +/-0.036 Hz | -103 | MW/0.1 Hz
[9 empty] | Up | Ramp Direction during frequency recovery period
[20 empty] | Frequency, Actual Interchange, Adjustment Data, Bias and Load used in the evaluation | [12 empty] | 20 to 52 second Average Period Evaluation
[5 empty] | Initial Response P.U. Performance | 1.078 | P.U. |  | 0.84493 | P.U. Sustained Response P.U. Performance | [26 empty] | Initial P.U. Performance Bias | 0.99172 | P.U.
[37 empty] | Initial P.U. Performance Adjusted for Bias | 1.0425 | P.U.
[9 empty] | Initial | [13 empty] | JOU | Non- |  |  | Transferred | Contingent | [7 empty] | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  | Actual
[7 empty] | Bias |  | Measure |  |  | Average | Average |  | Average | [6 empty] | Net | Dynamic | Conforming | Pumped | Future | Frequency | BA | BA | BA | Expected Primary |  |  |  | Net | Dynamic | Conforming | Pumped |  | Frequency | BA | BA | BA |  | Adjusted Net | Actual | Primary
[7 empty] | (EPFR) | (TC) | Final |  |  | Output | Target |  | Ramp | [6 empty] | Actual | Schedules | Load | Hydro | Adjustment | Response | Lost Generation | Bias | Load | Freq Response |  |  |  | Actual | Schedules | Load | Hydro |  | Response | Lost Generation | Bias | Load |  | Actual | Primary | Freq Response
|  |  |  | Value B |  |  | Expected | Delayed | Expected |  | Recovery | During | During | Recovery | During | [5 empty] | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) |  | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | Based on Bias Setting |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) |  | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange | Freq Response | Beta
|  |  |  | 20 to 52 sec |  |  | Primary | Delivery | Primary | Average | Period | Recovery | Recovery | Period | Recovery |  |  |  |  | T | Hz | MW | MW | MW | MW |  | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW |  | T | Hz | MW | MW | MW | MW |  | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW | MW | MW/0.1 Hz
|  | Frequency | Interchange | Average | Average |  | Frequency | Frequency | Frequency | Ramp | Target | Period | Period | Ramp | Period
| T | Hz | MW | Frequency | MW |  | Response | Response | Response | MW/scan | MW | MW | MW | MW | MW
T-72 sec | 40098.1015 | 60.019 | 3671.6272 |  |  | 3090 | -19.571 | -6.8499 | [10 empty] | T-72 sec | 40098.1015 | 60.019 | 3671.6272 | 350 | -160.4472 | 0 |  | 10 | 15 | -103 | 7640.58 | -19.571 | T-72 sec | 40098.1015 | [14 empty] | 0.019001
T-70 sec | 40098.1016 | 60.027 | 3671.189 |  |  | 3090 | -27.8104 | -14.1861 | [10 empty] | T-70 sec | 40098.1016 | 60.027 | 3671.189 | 350 | -160.4472 | 0 |  | 10 | 15 | -103 | 7640.91 | -27.8104 | T-70 sec | 40098.1016 | [14 empty] | 0.027
T-68 sec | 40098.1016 | 60.026 | 3668.6106 |  |  | 3090 | -26.781 | -18.5943 | [10 empty] | T-68 sec | 40098.1016 | 60.026 | 3668.6106 | 350 | -160.4472 | 0 |  | 10 | 15 | -103 | 7641.24 | -26.781 | T-68 sec | 40098.1016 | [14 empty] | 0.026001
T-66 sec | 40098.1016 | 60.026 | 3665.2322 |  |  | 3090 | -26.781 | -21.4596 | [10 empty] | T-66 sec | 40098.1016 | 60.026 | 3665.2322 | 350 | -160.4472 | 0 |  | 10 | 15 | -103 | 7641.57 | -26.781 | T-66 sec | 40098.1016 | [14 empty] | 0.026001
T-64 sec | 40098.1016 | 60.022 | 3664.4951 |  |  | 3090 | -22.6593 | -21.8795 | [10 empty] | T-64 sec | 40098.1016 | 60.022 | 3664.4951 | 350 | -163.9586 | 0 |  | 10 | 15 | -103 | 7641.9 | -22.6593 | T-64 sec | 40098.1016 | [14 empty] | 0.021999
T-62 sec | 40098.1016 | 60.019 | 3666.0618 |  |  | 3090 | -19.571 | -21.0716 | [10 empty] | T-62 sec | 40098.1016 | 60.019 | 3666.0618 | 350 | -163.9586 | 0 |  | 10 | 15 | -103 | 7642.23 | -19.571 | T-62 sec | 40098.1016 | [14 empty] | 0.019001
T-60 sec | 40098.1017 | 60.017 | 3666.8208 |  |  | 3090 | -17.5082 | -19.8244 |  | -0.10028 | 3666.8208 | [7 empty] | T-60 sec | 40098.1017 | 60.017 | 3666.8208 | 350 | -163.9586 | 0 |  | 10 | 15 | -103 | 7642.56 | -17.5082 | T-60 sec | 40098.1017 | [14 empty] | 0.016998
T-58 sec | 40098.1017 | 60.019 | 3666.7874 |  |  | 3090 | -19.571 | -19.7357 |  | -0.10028 | 3666.8092 | [7 empty] | T-58 sec | 40098.1017 | 60.019 | 3666.7874 | 350 | -163.9586 | 0 |  | 10 | 15 | -103 | 7642.89 | -19.571 | T-58 sec | 40098.1017 | [14 empty] | 0.019001
T-56 sec | 40098.1017 | 60.02 | 3670.4536 |  |  | 3090 | -20.6005 | -20.0384 |  | -0.10028 | 3666.4062 | [7 empty] | T-56 sec | 40098.1017 | 60.02 | 3670.4536 | 350 | -163.9586 | 0 |  | 10 | 15 | -103 | 7643.22 | -20.6005 | T-56 sec | 40098.1017 | [14 empty] | 0.02
T-54 sec | 40098.1017 | 60.019 | 3670.2668 |  |  | 3090 | -19.571 | -19.8748 |  | -0.10028 | 3666.4695 | [7 empty] | T-54 sec | 40098.1017 | 60.019 | 3670.2668 | 350 | -166.0724 | 0 |  | 10 | 15 | -103 | 7643.55 | -19.571 | T-54 sec | 40098.1017 | [14 empty] | 0.019001
T-52 sec | 40098.1018 | 60.021 | 3671.668 |  |  | 3090 | -21.6299 | -20.4891 |  | -0.10028 | 3665.755 | [7 empty] | T-52 sec | 40098.1018 | 60.021 | 3671.668 | 350 | -166.0724 | 0 |  | 10 | 15 | -103 | 7643.88 | -21.6299 | T-52 sec | 40098.1018 | [14 empty] | 0.021
T-50 sec | 40098.1018 | 60.021 | 3672.4932 |  |  | 3090 | -21.6299 | -20.8884 |  | -0.10028 | 3665.2554 | [7 empty] | T-50 sec | 40098.1018 | 60.021 | 3672.4932 | 350 | -166.0724 | 0 |  | 10 | 15 | -103 | 7644.21 | -21.6299 | T-50 sec | 40098.1018 | [14 empty] | 0.021
T-48 sec | 40098.1018 | 60.021 | 3672.6851 |  |  | 3090 | -21.6299 | -21.1479 |  | -0.10028 | 3664.8956 | [7 empty] | T-48 sec | 40098.1018 | 60.021 | 3672.6851 | 350 | -166.0724 | 0 |  | 10 | 15 | -103 | 7644.54 | -21.6299 | T-48 sec | 40098.1018 | [14 empty] | 0.021
T-46 sec | 40098.1018 | 60.019 | 3672.8574 |  |  | 3090 | -19.571 | -20.596 |  | -0.10028 | 3665.3472 | [7 empty] | T-46 sec | 40098.1018 | 60.019 | 3672.8574 | 350 | -166.0724 | 0 |  | 10 | 15 | -103 | 7644.87 | -19.571 | T-46 sec | 40098.1018 | [14 empty] | 0.019001
T-44 sec | 40098.1019 | 60.018 | 3672.1641 |  |  | 3090 | -18.5416 | -19.877 |  | -0.10028 | 3665.966 | [7 empty] | T-44 sec | 40098.1019 | 60.018 | 3672.1641 | 350 | -163.7666 | 0 |  | 10 | 15 | -103 | 7645.2 | -18.5416 | T-44 sec | 40098.1019 | [14 empty] | 0.018002
T-42 sec | 40098.1019 | 60.022 | 3671.4131 |  |  | 3090 | -22.6593 | -20.8508 |  | -0.10028 | 3664.8918 | [7 empty] | T-42 sec | 40098.1019 | 60.022 | 3671.4131 | 350 | -163.7666 | 0 |  | 10 | 15 | -103 | 7645.53 | -22.6593 | T-42 sec | 40098.1019 | [14 empty] | 0.021999
T-40 sec | 40098.1019 | 60.031 | 3669.9829 |  |  | 3090 | -31.9282 | -24.7279 |  | -0.10028 | 3660.9145 | [7 empty] | T-40 sec | 40098.1019 | 60.031 | 3669.9829 | 350 | -163.7666 | 0 |  | 10 | 15 | -103 | 7645.86 | -31.9282 | T-40 sec | 40098.1019 | [14 empty] | 0.030998
T-38 sec | 40098.1019 | 60.037 | 3666.4673 |  |  | 3090 | -38.1087 | -29.4112 |  | -0.10028 | 3656.1309 | [7 empty] | T-38 sec | 40098.1019 | 60.037 | 3666.4673 | 350 | -163.7666 | 0 |  | 10 | 15 | -103 | 7646.19 | -38.1087 | T-38 sec | 40098.1019 | [14 empty] | 0.036999 | -103
T-36 sec | 40098.1019 | 60.037 | 3663.7581 |  |  | 3090 | -38.1087 | -32.4553 |  | -0.10028 | 3652.9865 | [7 empty] | T-36 sec | 40098.1019 | 60.037 | 3663.7581 | 350 | -163.7666 | 0 |  | 10 | 15 | -103 | 7646.52 | -38.1087 | T-36 sec | 40098.1019 | [14 empty] | 0.036999 | -103
T-34 sec | 40098.102 | 60.036 | 3661.5991 |  |  | 3090 | -37.0793 | -34.0737 |  | -0.10028 | 3651.2678 | [7 empty] | T-34 sec | 40098.102 | 60.036 | 3661.5991 | 350 | -165.1017 | 0 |  | 10 | 15 | -103 | 7646.85 | -37.0793 | T-34 sec | 40098.102 | [14 empty] | 0.035999
T-32 sec | 40098.102 | 60.037 | 3660.6724 |  |  | 3090 | -38.1087 | -35.486 |  | -0.10028 | 3649.7553 | [7 empty] | T-32 sec | 40098.102 | 60.037 | 3660.6724 | 350 | -165.1017 | 0 |  | 10 | 15 | -103 | 7647.18 | -38.1087 | T-32 sec | 40098.102 | [14 empty] | 0.036999 | -103
T-30 sec | 40098.102 | 60.046 | 3651.4917 |  |  | 3090 | -47.3815 | -39.6494 |  | -0.10028 | 3645.4916 | [7 empty] | T-30 sec | 40098.102 | 60.046 | 3651.4917 | 350 | -165.1017 | 0 |  | 10 | 15 | -103 | 7647.51 | -47.3815 | T-30 sec | 40098.102 | [14 empty] | 0.046001 | -103
T-28 sec | 40098.102 | 60.048 | 3649.1904 |  |  | 3090 | -49.4403 | -43.0762 |  | -0.10028 | 3641.9644 | [7 empty] | T-28 sec | 40098.102 | 60.048 | 3649.1904 | 350 | -165.1017 | 0 |  | 10 | 15 | -103 | 7647.84 | -49.4403 | T-28 sec | 40098.102 | [14 empty] | 0.048 | -103
T-26 sec | 40098.1021 | 60.048 | 3650.0251 |  |  | 3090 | -49.4403 | -45.3037 |  | -0.10028 | 3639.6367 | [7 empty] | T-26 sec | 40098.1021 | 60.048 | 3650.0251 | 350 | -165.1017 | 0 |  | 10 | 15 | -103 | 7648.17 | -49.4403 | T-26 sec | 40098.1021 | [14 empty] | 0.048 | -103
T-24 sec | 40098.1021 | 60.043 | 3648.2463 |  |  | 3090 | -44.2892 | -44.9486 |  | -0.10028 | 3639.8915 | [7 empty] | T-24 sec | 40098.1021 | 60.043 | 3648.2463 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7648.5 | -44.2892 | T-24 sec | 40098.1021 | [14 empty] | 0.042999 | -103
T-22 sec | 40098.1021 | 60.041 | 3649.512 |  |  | 3090 | -42.2304 | -43.9972 |  | -0.10028 | 3640.7426 | [7 empty] | T-22 sec | 40098.1021 | 60.041 | 3649.512 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7648.83 | -42.2304 | T-22 sec | 40098.1021 | [14 empty] | 0.041 | -103
T-20 sec | 40098.1021 | 60.041 | 3654.2944 |  |  | 3090 | -42.2304 | -43.3788 |  | -0.10028 | 3641.2607 | [7 empty] | T-20 sec | 40098.1021 | 60.041 | 3654.2944 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7649.16 | -42.2304 | T-20 sec | 40098.1021 | [14 empty] | 0.041 | -103
T-18 sec | 40098.1022 | 60.041 | 3655.0068 |  |  | 3090 | -42.2304 | -42.9769 |  | -0.10028 | 3641.5624 | [7 empty] | T-18 sec | 40098.1022 | 60.041 | 3655.0068 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7649.49 | -42.2304 | T-18 sec | 40098.1022 | [14 empty] | 0.041 | -103
T-16 sec | 40098.1022 | 60.039 | 3651.8743 | 60.0421 | 3647.0624 | 3090 | -40.1715 | -41.995 |  | -0.10028 | 3642.444 | [7 empty] | T-16 sec | 40098.1022 | 60.039 | 3651.8743 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7649.82 | -40.1715 | T-16 sec | 40098.1022 | 60.0421 | 3647.0624 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.975 | -43.389 |  |  |  | 0.039001 | -103
T-14 sec | 40098.1022 | 60.041 | 3651.0593 | 60.0421 | 3647.0624 | 3090 | -42.2304 | -42.0774 |  | -0.10028 | 3642.2613 | [7 empty] | T-14 sec | 40098.1022 | 60.041 | 3651.0593 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.15 | -42.2304 | T-14 sec | 40098.1022 | 60.0421 | 3647.0624 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.975 | -43.389 |  |  |  | 0.041 | -103
T-12 sec | 40098.1022 | 60.043 | 3649.187 | 60.0421 | 3647.0624 | 3090 | -44.2892 | -42.8515 |  | -0.10028 | 3641.3868 | [7 empty] | T-12 sec | 40098.1022 | 60.043 | 3649.187 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.48 | -44.2892 | T-12 sec | 40098.1022 | 60.0421 | 3647.0624 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.975 | -43.389 |  |  |  | 0.042999 | -103
T-10 sec | 40098.1022 | 60.045 | 3648.2363 | 60.0421 | 3647.0624 | 3090 | -46.3481 | -44.0753 |  | -0.10028 | 3640.0628 | [7 empty] | T-10 sec | 40098.1022 | 60.045 | 3648.2363 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.81 | -46.3481 | T-10 sec | 40098.1022 | 60.0421 | 3647.0624 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.975 | -43.389 |  |  |  | 0.044998 | -103
T-08 sec | 40098.1023 | 60.046 | 3645.387 | 60.0421 | 3647.0624 | 3090 | -47.3815 | -45.2325 |  | -0.10028 | 3638.8053 | [7 empty] | T-08 sec | 40098.1023 | 60.046 | 3645.387 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7651.14 | -47.3815 | T-08 sec | 40098.1023 | 60.0421 | 3647.0624 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.975 | -43.389 |  |  |  | 0.046001 | -103
T-06 sec | 40098.1023 | 60.041 | 3644.6277 | 60.0421 | 3647.0624 | 3090 | -42.2304 | -44.1817 |  | -0.10028 | 3639.7558 | [7 empty] | T-06 sec | 40098.1023 | 60.041 | 3644.6277 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7651.47 | -42.2304 | T-06 sec | 40098.1023 | 60.0421 | 3647.0624 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.975 | -43.389 |  |  |  | 0.041 | -103
T-04 sec | 40098.1023 | 60.041 | 3645.4458 | 60.0421 | 3647.0624 | 3090 | -42.2304 | -43.4988 |  | -0.10028 | 3640.3385 | [7 empty] | T-04 sec | 40098.1023 | 60.041 | 3645.4458 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7651.8 | -42.2304 | T-04 sec | 40098.1023 | 60.0421 | 3647.0624 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.975 | -43.389 |  |  |  | 0.041 | -103
T-02 sec | 40098.1023 | 60.041 | 3640.6821 | 60.0421 | 3647.0624 | 3090 | -42.2304 | -43.0548 |  | -0.10028 | 3640.6821 | [7 empty] | T-02 sec | 40098.1023 | 60.041 | 3640.6821 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7652.13 | -42.2304 | T-02 sec | 40098.1023 | 60.0421 | 3647.0624 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7650.975 | -43.389 |  |  |  | 0.041 | -103
T+0 sec | 40098.1024 | 60.039 | 3641.1912 |  |  | 3090 | -40.1715 | -42.0457 |  | 0 | 3641.6913 | [7 empty] | T+0 sec | 40098.1024 | 60.039 | 3641.1912 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7652.46 | -40.1715 | T+0 sec | 40098.1024 | [14 empty] | 0.039001 | -103
T+02 sec | 40098.1024 | 59.978 | 3659.4648 |  |  | 3090 | 22.6593 | -19.3989 |  | 0.5823 | 3649.9203 | 3650.328 | 3645.8058 | 3673.8443 | 3673.8443 |  |  |  | T+02 sec | 40098.1024 | 59.978 | 3659.4648 | 350 | -165.4764 | 0 |  | 10 | 15 | -103 | 7652.79 | 22.6593 | T+02 sec | 40098.1024 | [14 empty] | 0.021999
T+04 sec | 40098.1024 | 59.852 | 3696.3623 |  |  | 3090 | 152.4388 | 40.7443 |  | 0.5823 | 3710.6458 | 3665.6728 | 3667.4192 | 3674.4266 | 3674.1354 |  |  |  | T+04 sec | 40098.1024 | 59.852 | 3696.3623 | 335 | -211.256 | 1 |  | 10 | 0 | -103 | 7616 | 152.4388 | T+04 sec | 40098.1024 | [12 empty] | 64.8822 | -34.1262 | 0.148 | -103
T+06 sec | 40098.1024 | 59.836 | 3734.9043 |  |  | 3090 | 168.9215 | 85.6063 |  | 0.5823 | 3756.0902 | 3682.9807 | 3689.5869 | 3675.0089 | 3674.4266 |  |  |  | T+06 sec | 40098.1024 | 59.836 | 3734.9043 | 335 | -214.3467 | 1 |  | 10 | 0 | -103 | 7626 | 168.9215 | T+06 sec | 40098.1024 | [12 empty] | 103.4242 | -50.175 | 0.164 | -103
T+08 sec | 40098.1025 | 59.869 | 3734.6726 |  |  | 3090 | 134.9305 | 102.8698 |  | 0.5823 | 3773.936 | 3693.319 | 3706.4567 | 3675.5912 | 3674.7177 |  |  |  | T+08 sec | 40098.1025 | 59.869 | 3734.6726 | 335 | -214.3467 | 1 |  | 10 | 0 | -103 | 7632 | 134.9305 | T+08 sec | 40098.1025 | [12 empty] | 103.1925 | -59.6055 | 0.131 | -103
T+10 sec | 40098.1025 | 59.892 | 3737.1567 |  |  | 3090 | 111.2418 | 105.8 |  | 0.5823 | 3777.4485 | 3700.6253 | 3718.2887 | 3676.1735 | 3675.0089 |  |  |  | T+10 sec | 40098.1025 | 59.892 | 3737.1567 | 335 | -214.3467 | 1 |  | 10 | 0 | -103 | 7632 | 111.2418 | T+10 sec | 40098.1025 | [12 empty] | 105.6766 | -70.3915 | 0.108 | -103
T+12 sec | 40098.1025 | 59.891 | 3761.2495 |  |  | 3090 | 112.2712 | 108.0649 |  | 0.5823 | 3780.2957 | 3709.2859 | 3727.1468 | 3676.7558 | 3675.3 |  |  |  | T+12 sec | 40098.1025 | 59.891 | 3761.2495 | 335 | -214.3467 | 2 |  | 10 | 0 | -103 | 7632 | 112.2712 | T+12 sec | 40098.1025 | [12 empty] | 129.7694 | -85.8681 | 0.109 | -103
T+14 sec | 40098.1025 | 59.88 | 3766.113 |  |  | 3090 | 123.5989 | 113.5018 |  | 0.5823 | 3786.3149 | 3716.3893 | 3734.5428 | 3677.3381 | 3675.5912 |  |  |  | T+14 sec | 40098.1025 | 59.88 | 3766.113 | 335 | -214.3467 | 3 |  | 10 | 0 | -103 | 7632 | 123.5989 | T+14 sec | 40098.1025 | [12 empty] | 134.6329 | -83.0431 | 0.12 | -103
T+16 sec | 40098.1025 | 59.876 | 3766.1938 |  |  | 3090 | 127.7206 | 118.4784 |  | 0.5823 | 3791.8738 | 3721.9231 | 3740.9129 | 3677.9204 | 3675.8823 |  |  |  | T+16 sec | 40098.1025 | 59.876 | 3766.1938 | 335 | -212.1727 | 4 |  | 10 | 0 | -103 | 7632 | 127.7206 | T+16 sec | 40098.1025 | [12 empty] | 134.7137 | -81.0914 | 0.124 | -103
T+18 sec | 40098.1026 | 59.875 | 3768.877 |  |  | 3090 | 128.75 | 122.0734 |  | 0.5823 | 3796.0511 | 3726.6185 | 3746.4267 | 3678.5027 | 3676.1735 |  |  |  | T+18 sec | 40098.1026 | 59.875 | 3768.877 | 335 | -212.1727 | 5 |  | 10 | 0 | -103 | 7632 | 128.75 | T+18 sec | 40098.1026 | [12 empty] | 137.3968 | -82.2119 | 0.125 | -103
T+20 sec | 40098.1026 | 59.883 | 3769.925 | 59.8891 | 3788.3545 | 3090 | 120.5106 | 121.5264 | 3789.6601 | 0.5823 | 3796.0864 | 3730.5555 | 3750.9413 | 3679.085 | 3676.4646 |  |  |  | T+20 sec | 40098.1026 | 59.883 | 3769.925 | 335 | -212.1727 | 6 |  | 10 | 0 | -103 | 7632 | 120.5106 | T+20 sec | 40098.1026 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 138.4449 | -87.0034 | 0.117 | -103
T+22 sec | 40098.1026 | 59.887 | 3780.6206 | 59.8891 | 3788.3545 | 3090 | 116.3889 | 119.7283 | 3789.6601 | 0.5823 | 3794.8706 | 3734.7276 | 3754.602 | 3679.6673 | 3676.7558 |  |  |  | T+22 sec | 40098.1026 | 59.887 | 3780.6206 | 335 | -212.1727 | 7 |  | 10 | 0 | -103 | 7632 | 116.3889 | T+22 sec | 40098.1026 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 149.1405 | -96.1426 | 0.113 | -103
T+24 sec | 40098.1026 | 59.886 | 3781.5918 | 59.8891 | 3788.3545 | 3090 | 117.4184 | 118.9198 | 3789.6601 | 0.5823 | 3794.6444 | 3738.3325 | 3757.6822 | 3680.2496 | 3677.0469 |  |  |  | T+24 sec | 40098.1026 | 59.886 | 3781.5918 | 335 | -212.1727 | 8 |  | 10 | 0 | -103 | 7632 | 117.4184 | T+24 sec | 40098.1026 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 150.1117 | -96.1492 | 0.114 | -103
T+26 sec | 40098.1027 | 59.885 | 3782.4995 | 59.8891 | 3788.3545 | 3090 | 118.4517 | 118.756 | 3789.6601 | 0.5823 | 3795.0629 | 3741.4873 | 3760.3523 | 3680.8319 | 3677.3381 |  |  |  | T+26 sec | 40098.1027 | 59.885 | 3782.4995 | 335 | -215.5982 | 9 |  | 10 | 0 | -103 | 7632 | 118.4517 | T+26 sec | 40098.1027 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 151.0194 | -96.113 | 0.115 | -103
T+28 sec | 40098.1027 | 59.887 | 3784.9619 | 59.8891 | 3788.3545 | 3090 | 116.3889 | 117.9275 | 3789.6601 | 0.5823 | 3794.8167 | 3744.3856 | 3762.6499 | 3681.4142 | 3677.6293 |  |  |  | T+28 sec | 40098.1027 | 59.887 | 3784.9619 | 335 | -215.5982 | 10 |  | 10 | 0 | -103 | 7632 | 116.3889 | T+28 sec | 40098.1027 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 153.4818 | -98.9412 | 0.113 | -103
T+30 sec | 40098.1027 | 59.888 | 3784.7297 | 59.8891 | 3788.3545 | 3090 | 115.3595 | 117.0287 | 3789.6601 | 0.5823 | 3794.5002 | 3746.9071 | 3764.6405 | 3681.9965 | 3677.9204 |  |  |  | T+30 sec | 40098.1027 | 59.888 | 3784.7297 | 335 | -215.5982 | 11 |  | 10 | 0 | -103 | 7632 | 115.3595 | T+30 sec | 40098.1027 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 153.2496 | -99.4322 | 0.112 | -103
T+32 sec | 40098.1027 | 59.89 | 3784.4189 | 59.8891 | 3788.3545 | 3090 | 113.3006 | 115.7239 | 3789.6601 | 0.5823 | 3793.7777 | 3749.1137 | 3766.3545 | 3682.5788 | 3678.2116 |  |  |  | T+32 sec | 40098.1027 | 59.89 | 3784.4189 | 335 | -215.5982 | 12 |  | 10 | 0 | -103 | 7632 | 113.3006 | T+32 sec | 40098.1027 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 152.9388 | -100.5344 | 0.11 | -103
T+34 sec | 40098.1028 | 59.895 | 3788.0723 | 59.8891 | 3788.3545 | 3090 | 108.1495 | 113.0729 | 3789.6601 | 0.5823 | 3791.709 | 3751.2781 | 3767.7631 | 3683.1611 | 3678.5027 |  |  |  | T+34 sec | 40098.1028 | 59.895 | 3788.0723 | 335 | -215.5982 | 13 |  | 10 | 0 | -103 | 7632 | 108.1495 | T+34 sec | 40098.1028 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 156.5921 | -106.4349 | 0.105 | -103
T+36 sec | 40098.1028 | 59.894 | 3788.3276 | 59.8891 | 3788.3545 | 3090 | 109.179 | 111.71 | 3789.6601 | 0.5823 | 3790.9284 | 3753.228 | 3768.9823 | 3683.7434 | 3678.7939 |  |  |  | T+36 sec | 40098.1028 | 59.894 | 3788.3276 | 335 | -218.3273 | 14 |  | 10 | 0 | -103 | 7632 | 109.179 | T+36 sec | 40098.1028 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 156.8475 | -105.8892 | 0.106 | -103
T+38 sec | 40098.1028 | 59.893 | 3788.8684 | 59.8891 | 3788.3545 | 3090 | 110.2084 | 111.1844 | 3789.6601 | 0.5823 | 3790.9851 | 3755.0101 | 3770.0824 | 3684.3257 | 3679.085 |  |  |  | T+38 sec | 40098.1028 | 59.893 | 3788.8684 | 335 | -218.3273 | 15 |  | 10 | 0 | -103 | 7632 | 110.2084 | T+38 sec | 40098.1028 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 157.3883 | -105.5421 | 0.107 | -103
T+40 sec | 40098.1028 | 59.894 | 3788.4719 | 59.8891 | 3788.3545 | 3090 | 109.179 | 110.4825 | 3789.6601 | 0.5823 | 3790.8655 | 3756.6035 | 3771.0721 | 3684.908 | 3679.3762 |  |  |  | T+40 sec | 40098.1028 | 59.894 | 3788.4719 | 335 | -218.3273 | 16 |  | 10 | 0 | -103 | 7632 | 109.179 | T+40 sec | 40098.1028 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 156.9918 | -105.9866 | 0.106 | -103
T+42 sec | 40098.1028 | 59.894 | 3792.2756 | 59.8891 | 3788.3545 | 3090 | 109.179 | 110.0263 | 3789.6601 | 0.5823 | 3790.9916 | 3758.2249 | 3771.9775 | 3685.4903 | 3679.6673 |  |  |  | T+42 sec | 40098.1028 | 59.894 | 3792.2756 | 335 | -218.3273 | 16 |  | 10 | 0 | -103 | 7632 | 109.179 | T+42 sec | 40098.1028 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 160.7955 | -108.5545 | 0.106 | -103
T+44 sec | 40098.1029 | 59.891 | 3793.0745 | 59.8891 | 3788.3545 | 3090 | 112.2712 | 110.812 | 3789.6601 | 0.5823 | 3792.3596 | 3759.7401 | 3772.8637 | 3686.0726 | 3679.9585 |  |  |  | T+44 sec | 40098.1029 | 59.891 | 3793.0745 | 335 | -218.3273 | 16 |  | 10 | 0 | -103 | 7632 | 112.2712 | T+44 sec | 40098.1029 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 161.5943 | -106.9266 | 0.109 | -103
T+46 sec | 40098.1029 | 59.89 | 3794.3743 | 59.8891 | 3788.3545 | 3090 | 113.3006 | 111.683 | 3789.6601 | 0.5823 | 3793.8129 | 3761.1832 | 3773.7366 | 3686.6549 | 3680.2496 |  |  |  | T+46 sec | 40098.1029 | 59.89 | 3794.3743 | 335 | -217.3794 | 16 |  | 10 | 0 | -103 | 7632 | 113.3006 | T+46 sec | 40098.1029 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 162.8941 | -107.0785 | 0.11 | -103
T+48 sec | 40098.1029 | 59.885 | 3799.4277 | 59.8891 | 3788.3545 | 3090 | 118.4517 | 114.0521 | 3789.6601 | 0.5823 | 3796.7643 | 3762.713 | 3774.6577 | 3687.2372 | 3680.5408 |  |  |  | T+48 sec | 40098.1029 | 59.885 | 3799.4277 | 335 | -217.3794 | 16 |  | 10 | 0 | -103 | 7632 | 118.4517 | T+48 sec | 40098.1029 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 167.9476 | -106.8866 | 0.115 | -103
T+50 sec | 40098.1029 | 59.885 | 3800.4275 | 59.8891 | 3788.3545 | 3090 | 118.4517 | 115.5919 | 3789.6601 | 0.5823 | 3798.8865 | 3764.1636 | 3775.5896 | 3687.8195 | 3680.8319 |  |  |  | T+50 sec | 40098.1029 | 59.885 | 3800.4275 | 335 | -217.3794 | 16 |  | 10 | 0 | -103 | 7632 | 118.4517 | T+50 sec | 40098.1029 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 168.9474 | -107.5229 | 0.115 | -103
T+52 sec | 40098.103 | 59.888 | 3799.9592 | 59.8891 | 3788.3545 | 3090 | 115.3595 | 115.5106 | 3789.6601 | 0.5823 | 3799.3874 | 3765.4893 | 3776.471 | 3688.4018 | 3681.1231 |  |  |  | T+52 sec | 40098.103 | 59.888 | 3799.9592 | 335 | -217.3794 | 16 |  | 10 | 0 | -103 | 7632 | 115.3595 | T+52 sec | 40098.103 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 |  | 10 | 0 | -103 | 7632 | 114.2087 | 3781.9865 | 168.4791 | -109.3135 | 0.112 | -103
T+54 sec | 40098.103 | 59.887 | 3803.625 |  |  | 3090 | 116.3889 | 115.818 |  | 0.5823 | 3800.2771 | 3766.8513 | 3777.3212 | 3688.9842 | 3681.4142 |  |  |  | T+54 sec | 40098.103 | 59.887 | 3803.625 | 335 | -217.3794 | 16 |  | 10 | 0 | -103 | 7632 | 116.3889 | T+54 sec | 40098.103 | [12 empty] | 172.1449 | -110.9723 | 0.113 | -103
T+56 sec | 40098.103 | 59.888 | 3802.925 |  |  | 3090 | 115.3595 | 115.6575 |  | 0.5823 | 3800.699 | 3768.0952 | 3778.1273 | 3689.5665 | 3681.7054 |  |  |  | T+56 sec | 40098.103 | 59.888 | 3802.925 | 335 | -214.8304 | 16 |  | 10 | 0 | -103 | 7632 | 115.3595 | T+56 sec | 40098.103 | [12 empty] | 171.4449 | -111.2378 | 0.112 | -103
T+58 sec | 40098.103 | 59.888 | 3802.9509 |  |  | 3090 | 115.3595 | 115.5532 |  | 0.5823 | 3801.177 | 3769.2571 | 3778.8957 | 3690.1488 | 3681.9965 |  |  |  | T+58 sec | 40098.103 | 59.888 | 3802.9509 | 335 | -214.8304 | 16 |  | 10 | 0 | -103 | 7632 | 115.3595 | T+58 sec | 40098.103 | [12 empty] | 171.4708 | -111.2546 | 0.112 | -103
T+60 sec | 40098.1031 | 59.89 | 3804.3879 |  |  | 3090 | 113.3006 | 114.7648 |  | 0.5823 | 3800.9708 | 3770.3903 | 3779.6078 | 3690.7311 | 3682.2877 |  |  |  | T+60 sec | 40098.1031 | 59.89 | 3804.3879 | 335 | -214.8304 | 16 |  | 10 | 0 | -103 | 7632 | 113.3006 | T+60 sec | 40098.1031 | [12 empty] | 172.9078 | -113.661 | 0.11 | -103
T+62 sec | 40098.1031 | 59.889 | 3805.4961 |  |  | 3090 | 114.33 | 114.6126 |  | 0.5823 | 3801.401 | 3771.4874 | 3780.2888 | 3691.3134 | 3682.5788 |  |  |  | T+62 sec | 40098.1031 | 59.889 | 3805.4961 | 335 | -214.8304 | 16 |  | 10 | 0 | -103 | 7632 | 114.33 | T+62 sec | 40098.1031 | [12 empty] | 174.016 | -113.6429 | 0.111 | -103
T+64 sec | 40098.1031 | 59.882 | 3805.6167 |  |  | 3090 | 121.54 | 117.0372 |  | 0.5823 | 3804.4079 | 3772.5216 | 3781.0197 | 3691.8957 | 3682.87 |  |  |  | T+64 sec | 40098.1031 | 59.882 | 3805.6167 | 335 | -214.8304 | 16 |  | 10 | 0 | -103 | 7632 | 121.54 | T+64 sec | 40098.1031 | [12 empty] | 174.1366 | -108.7502 | 0.118 | -103
T+66 sec | 40098.1031 | 59.873 | 3809.2373 |  |  | 3090 | 130.8089 | 121.8573 |  | 0.5823 | 3809.8102 | 3773.6015 | 3781.8665 | 3692.478 | 3683.1611 |  |  |  | T+66 sec | 40098.1031 | 59.873 | 3809.2373 | 335 | -227.6559 | 16 |  | 10 | 0 | -103 | 7631 | 130.8089 | T+66 sec | 40098.1031 | [12 empty] | 177.7572 | -105.1046 | 0.127 | -103
T+68 sec | 40098.1031 | 59.857 | 3811.5029 |  |  | 3090 | 147.2916 | 130.7593 |  | 0.5823 | 3819.2945 | 3774.6844 | 3782.9358 | 3693.0603 | 3683.4523 |  |  |  | T+68 sec | 40098.1031 | 59.857 | 3811.5029 | 335 | -227.6559 | 16 |  | 10 | 0 | -103 | 7625 | 147.2916 | T+68 sec | 40098.1031 | [12 empty] | 180.0228 | -97.243 | 0.143 | -103
T+70 sec | 40098.1032 | 59.849 | 3814.8623 |  |  | 3090 | 155.531 | 139.4294 |  | 0.5823 | 3828.5469 | 3775.8004 | 3784.2028 | 3693.6426 | 3683.7434 |  |  |  | T+70 sec | 40098.1032 | 59.849 | 3814.8623 | 335 | -227.6559 | 16 |  | 10 | 0 | -103 | 7623 | 155.531 | T+70 sec | 40098.1032 | [12 empty] | 183.3822 | -94.9546 | 0.151 | -103
T+72 sec | 40098.1032 | 59.852 | 3815.8889 |  |  | 3090 | 152.4388 | 143.9827 |  | 0.5823 | 3833.6825 | 3776.8839 | 3785.5401 | 3694.2249 | 3684.0346 |  |  |  | T+72 sec | 40098.1032 | 59.852 | 3815.8889 | 335 | -227.6559 | 16 |  | 10 | 0 | -103 | 7621 | 152.4388 | T+72 sec | 40098.1032 | [12 empty] | 184.4088 | -96.9939 | 0.148 | -103
T+74 sec | 40098.1032 | 59.858 | 3825.6426 |  |  | 3090 | 146.2582 | 144.7791 |  | 0.5823 | 3835.0613 | 3778.167 | 3786.8433 | 3694.8072 | 3684.3257 |  |  |  | T+74 sec | 40098.1032 | 59.858 | 3825.6426 | 335 | -227.6559 | 16 |  | 10 | 0 | -103 | 7623 | 146.2582 | T+74 sec | 40098.1032 | [12 empty] | 194.1624 | -105.4523 | 0.142 | -103
T+76 sec | 40098.1032 | 59.863 | 3826.0532 |  |  | 3090 | 141.1111 | 143.4953 |  | 0.5823 | 3834.3598 | 3779.3949 | 3788.0617 | 3695.3895 | 3684.6169 |  |  |  | T+76 sec | 40098.1032 | 59.863 | 3826.0532 | 335 | -225.0181 | 16 |  | 10 | 0 | -103 | 7625 | 141.1111 | T+76 sec | 40098.1032 | [12 empty] | 194.5731 | -108.6234 | 0.137 | -103
T+78 sec | 40098.1033 | 59.866 | 3826.0024 |  |  | 3090 | 138.0188 | 141.5785 |  | 0.5823 | 3833.0253 | 3780.5601 | 3789.1858 | 3695.9718 | 3684.908 |  |  |  | T+78 sec | 40098.1033 | 59.866 | 3826.0024 | 335 | -225.0181 | 16 |  | 10 | 0 | -103 | 7627 | 138.0188 | T+78 sec | 40098.1033 | [12 empty] | 194.5223 | -110.4462 | 0.134 | -103
T+80 sec | 40098.1033 | 59.865 | 3827.5239 |  |  | 3090 | 139.0483 | 140.6929 |  | 0.5823 | 3832.722 | 3781.7055 | 3790.2476 | 3696.5541 | 3685.1992 |  |  |  | T+80 sec | 40098.1033 | 59.865 | 3827.5239 | 335 | -225.0181 | 16 |  | 10 | 0 | -103 | 7628 | 139.0483 | T+80 sec | 40098.1033 | [12 empty] | 196.0438 | -110.6819 | 0.135 | -103
T+82 sec | 40098.1033 | 59.867 | 3826.7532 |  |  | 3090 | 136.9894 | 139.3967 |  | 0.5823 | 3832.0081 | 3782.7781 | 3791.2419 | 3697.1364 | 3685.4903 |  |  |  | T+82 sec | 40098.1033 | 59.867 | 3826.7532 | 335 | -225.0181 | 16 |  | 10 | 0 | -103 | 7628 | 136.9894 | T+82 sec | 40098.1033 | [12 empty] | 195.273 | -111.5052 | 0.133 | -103
T+84 sec | 40098.1033 | 59.866 | 3826.7834 |  |  | 3090 | 138.0188 | 138.9145 |  | 0.5823 | 3832.1081 | 3783.8015 | 3792.1923 | 3697.7187 | 3685.7815 |  |  |  | T+84 sec | 40098.1033 | 59.866 | 3826.7834 | 335 | -225.0181 | 16 |  | 10 | 0 | -103 | 7629 | 138.0188 | T+84 sec | 40098.1033 | [12 empty] | 195.3033 | -110.8896 | 0.134 | -103
T+86 sec | 40098.1034 | 59.871 | 3826.4536 |  |  | 3090 | 132.8717 | 136.7995 |  | 0.5823 | 3830.5754 | 3784.7709 | 3793.0646 | 3698.301 | 3686.0726 |  |  |  | T+86 sec | 40098.1034 | 59.871 | 3826.4536 | 335 | -228.3652 | 16 |  | 10 | 0 | -103 | 7630 | 132.8717 | T+86 sec | 40098.1034 | [12 empty] | 194.9735 | -113.9351 | 0.129 | -103
T+88 sec | 40098.1034 | 59.874 | 3825.7134 |  |  | 3090 | 129.7794 | 134.3425 |  | 0.5823 | 3828.7007 | 3785.6807 | 3793.8565 | 3698.8833 | 3686.3638 |  |  |  | T+88 sec | 40098.1034 | 59.874 | 3825.7134 | 335 | -228.3652 | 16 |  | 10 | 0 | -103 | 7631 | 129.7794 | T+88 sec | 40098.1034 | [12 empty] | 194.2332 | -115.5293 | 0.126 | -103
T+90 sec | 40098.1034 | 59.879 | 3823.8257 |  |  | 3090 | 124.6283 | 130.9425 |  | 0.5823 | 3825.8831 | 3786.5099 | 3794.5528 | 3699.4656 | 3686.6549 |  |  |  | T+90 sec | 40098.1034 | 59.879 | 3823.8257 | 335 | -228.3652 | 16 |  | 10 | 0 | -103 | 7635 | 124.6283 | T+90 sec | 40098.1034 | [12 empty] | 192.3455 | -117.914 | 0.121 | -103
T+92 sec | 40098.1034 | 59.88 | 3822.5054 |  |  | 3090 | 123.5989 | 128.3723 |  | 0.5823 | 3823.8951 | 3787.2758 | 3795.1771 | 3700.0479 | 3686.9461 |  |  |  | T+92 sec | 40098.1034 | 59.88 | 3822.5054 | 335 | -228.3652 | 16 |  | 10 | 0 | -103 | 7638 | 123.5989 | T+92 sec | 40098.1034 | [12 empty] | 191.0252 | -117.8265 | 0.12 | -103
T+94 sec | 40098.1034 | 59.883 | 3819.0811 |  |  | 3090 | 120.5106 | 125.6207 |  | 0.5823 | 3821.7259 | 3787.9384 | 3795.7302 | 3700.6302 | 3687.2372 |  |  |  | T+94 sec | 40098.1034 | 59.883 | 3819.0811 | 335 | -228.3652 | 16 |  | 10 | 0 | -103 | 7639 | 120.5106 | T+94 sec | 40098.1034 | [12 empty] | 187.6009 | -117.8947 | 0.117 | -103
T+96 sec | 40098.1035 | 59.886 | 3818.0552 |  |  | 3090 | 117.4184 | 122.7499 |  | 0.5823 | 3819.4373 | 3788.553 | 3796.214 | 3701.2125 | 3687.5284 |  |  |  | T+96 sec | 40098.1035 | 59.886 | 3818.0552 | 335 | -234.0753 | 16 |  | 10 | 0 | -103 | 7642 | 117.4184 | T+96 sec | 40098.1035 | [12 empty] | 186.575 | -119.5047 | 0.114 | -103
T+98 sec | 40098.1035 | 59.89 | 3816.8147 |  |  | 3090 | 113.3006 | 119.4426 |  | 0.5823 | 3816.7124 | 3789.1183 | 3796.624 | 3701.7948 | 3687.8195 |  |  |  | T+98 sec | 40098.1035 | 59.89 | 3816.8147 | 335 | -234.0753 | 16 |  | 10 | 0 | -103 | 7644 | 113.3006 | T+98 sec | 40098.1035 | [12 empty] | 185.3346 | -121.8298 | 0.11 | -103
T+100 sec | 40098.1035 | 59.892 | 3815.0098 |  |  | 3090 | 111.2418 | 116.5723 |  | 0.5823 | 3814.4244 | 3789.6259 | 3796.973 | 3702.3771 | 3688.1107 |  |  |  | T+100 sec | 40098.1035 | 59.892 | 3815.0098 | 335 | -234.0753 | 16 |  | 10 | 0 | -103 | 7645 | 111.2418 | T+100 sec | 40098.1035 | [12 empty] | 183.5296 | -122.2496 | 0.108 | -103
T+102 sec | 40098.1035 | 59.889 | 3813.7827 |  |  | 3090 | 114.3301 | 115.7875 |  | 0.5823 | 3814.2219 | 3790.0905 | 3797.3047 | 3702.9594 | 3688.4018 |  |  |  | T+102 sec | 40098.1035 | 59.889 | 3813.7827 | 335 | -234.0753 | 16 |  | 10 | 0 | -103 | 7647 | 114.3301 | T+102 sec | 40098.1035 | [12 empty] | 182.3026 | -119.0545 | 0.111 | -103
T+104 sec | 40098.1036 | 59.893 | 3811.8384 |  |  | 3090 | 110.2084 | 113.8348 |  | 0.5823 | 3812.8515 | 3790.5008 | 3797.598 | 3703.5417 | 3688.693 |  |  |  | T+104 sec | 40098.1036 | 59.893 | 3811.8384 | 335 | -234.0753 | 16 |  | 10 | 0 | -103 | 7648 | 110.2084 | T+104 sec | 40098.1036 | [12 empty] | 180.3582 | -120.9454 | 0.107 | -103
T+106 sec | 40098.1036 | 59.899 | 3809.6519 |  |  | 3090 | 104.0318 | 110.4038 |  | 0.5823 | 3810.0028 | 3790.8555 | 3797.8278 | 3704.124 | 3688.9842 |  |  |  | T+106 sec | 40098.1036 | 59.899 | 3809.6519 | 335 | -228.7982 | 16 |  | 10 | 0 | -103 | 7649 | 104.0318 | T+106 sec | 40098.1036 | [12 empty] | 178.1717 | -124.4851 | 0.101 | -103
T+108 sec | 40098.1036 | 59.903 | 3806.9722 |  |  | 3090 | 99.9101 | 106.731 |  | 0.5823 | 3806.9123 | 3791.1485 | 3797.9929 | 3704.7063 | 3689.2753 |  |  |  | T+108 sec | 40098.1036 | 59.903 | 3806.9722 | 335 | -228.7982 | 16 |  | 10 | 0 | -103 | 7650 | 99.9101 | T+108 sec | 40098.1036 | [12 empty] | 175.492 | -126.1395 | 0.097 | -103
T+110 sec | 40098.1036 | 59.902 | 3805.5933 |  |  | 3090 | 100.9396 | 104.704 |  | 0.5823 | 3805.4676 | 3791.4064 | 3798.1264 | 3705.2886 | 3689.5665 |  |  |  | T+110 sec | 40098.1036 | 59.902 | 3805.5933 | 335 | -228.7982 | 16 |  | 10 | 0 | -103 | 7651 | 100.9396 | T+110 sec | 40098.1036 | [12 empty] | 174.1131 | -124.2558 | 0.098 | -103
T+112 sec | 40098.1037 | 59.902 | 3804.1885 |  |  | 3090 | 100.9396 | 103.3864 |  | 0.5823 | 3804.7323 | 3791.6307 | 3798.2423 | 3705.8709 | 3689.8576 |  |  |  | T+112 sec | 40098.1037 | 59.902 | 3804.1885 | 335 | -228.7982 | 16 |  | 10 | 0 | -103 | 7652 | 100.9396 | T+112 sec | 40098.1037 | [12 empty] | 172.7083 | -123.2532 | 0.098 | -103
T+114 sec | 40098.1037 | 59.904 | 3796.0776 |  |  | 3090 | 98.8807 | 101.8094 |  | 0.5823 | 3803.7376 | 3791.7074 | 3798.3371 | 3706.4532 | 3690.1488 |  |  |  | T+114 sec | 40098.1037 | 59.904 | 3796.0776 | 335 | -228.7982 | 16 |  | 10 | 0 | -103 | 7653 | 98.8807 | T+114 sec | 40098.1037 | [12 empty] | 164.5975 | -119.1648 | 0.096001 | -103
T+116 sec | 40098.1037 | 59.907 | 3793.9751 |  |  | 3090 | 95.7885 | 99.7021 |  | 0.5823 | 3802.2126 | 3791.7458 | 3798.4027 | 3707.0355 | 3690.4399 |  |  |  | T+116 sec | 40098.1037 | 59.907 | 3793.9751 | 335 | -229.467 | 16 |  | 10 | 0 | -103 | 7654 | 95.7885 | T+116 sec | 40098.1037 | [12 empty] | 162.495 | -120.2564 | 0.092999 | -103
T+118 sec | 40098.1037 | 59.911 | 3792.1694 |  |  | 3090 | 91.6707 | 96.8911 |  | 0.5823 | 3799.9839 | 3791.7529 | 3798.4291 | 3707.6178 | 3690.7311 |  |  |  | T+118 sec | 40098.1037 | 59.911 | 3792.1694 | 335 | -229.467 | 16 |  | 10 | 0 | -103 | 7655 | 91.6707 | T+118 sec | 40098.1037 | [12 empty] | 160.6893 | -122.5458 | 0.089001 | -103
T+120 sec | 40098.1037 | 59.916 | 3791.502 |  |  | 3090 | 86.5196 | 93.2611 |  | 0.5823 | 3796.9362 | 3791.7487 | 3798.4046 | 3708.2001 | 3691.0222 |  |  |  | T+120 sec | 40098.1037 | 59.916 | 3791.502 | 335 | -229.467 | 16 |  | 10 | 0 | -103 | 7655 | 86.5196 | T+120 sec | 40098.1037 | [12 empty] | 160.0218 | -126.8757 | 0.084 | -103
T+122 sec | 40098.1038 | 59.916 | 3789.5337 |  |  | 3090 | 86.5196 | 90.9016 |  | 0.5823 | 3795.159 | 3791.713 | 3798.3523 | 3708.7824 | 3691.3134 |  |  |  | T+122 sec | 40098.1038 | 59.916 | 3789.5337 | 335 | -229.467 | 16 |  | 10 | 0 | -103 | 7656 | 86.5196 | T+122 sec | 40098.1038 | [12 empty] | 158.0536 | -125.3151 | 0.084 | -103
T+124 sec | 40098.1038 | 59.917 | 3788.1321 |  |  | 3090 | 85.4902 | 89.0076 |  | 0.5823 | 3793.8473 | 3791.6562 | 3798.2808 | 3709.3647 | 3691.6045 |  |  |  | T+124 sec | 40098.1038 | 59.917 | 3788.1321 | 335 | -229.467 | 16 |  | 10 | 0 | -103 | 7656 | 85.4902 | T+124 sec | 40098.1038 | [12 empty] | 156.6519 | -125.196 | 0.083 | -103
T+126 sec | 40098.1038 | 59.918 | 3784.5635 |  |  | 3090 | 84.4608 | 87.4162 |  | 0.5823 | 3792.8382 | 3791.5454 | 3798.1957 | 3709.947 | 3691.8957 |  |  |  | T+126 sec | 40098.1038 | 59.918 | 3784.5635 | 335 | -228.9802 | 16 |  | 10 | 0 | -103 | 7657 | 84.4608 | T+126 sec | 40098.1038 | [12 empty] | 153.0833 | -123.329 | 0.082001 | -103
T+128 sec | 40098.1038 | 59.92 | 3783.0283 |  |  | 3090 | 82.4019 | 85.6612 |  | 0.5823 | 3791.6655 | 3791.4143 | 3798.0953 | 3710.5293 | 3692.1868 |  |  |  | T+128 sec | 40098.1038 | 59.92 | 3783.0283 | 335 | -228.9802 | 16 |  | 10 | 0 | -103 | 7657 | 82.4019 | T+128 sec | 40098.1038 | [12 empty] | 151.5482 | -124.0906 | 0.080002 | -103
T+130 sec | 40098.1039 | 59.921 | 3781.7012 |  |  | 3090 | 81.3685 | 84.1588 |  | 0.5823 | 3790.7454 | 3791.2672 | 3797.9839 | 3711.1116 | 3692.478 |  |  |  | T+130 sec | 40098.1039 | 59.921 | 3781.7012 | 335 | -228.9802 | 16 |  | 10 | 0 | -103 | 7658 | 81.3685 | T+130 sec | 40098.1039 | [12 empty] | 150.221 | -124.0227 | 0.078999 | -103
T+132 sec | 40098.1039 | 59.92 | 3776.3584 |  |  | 3090 | 82.4019 | 83.5439 |  | 0.5823 | 3790.7128 | 3791.0446 | 3797.8754 | 3711.694 | 3692.7691 |  |  |  | T+132 sec | 40098.1039 | 59.92 | 3776.3584 | 335 | -228.9802 | 16 |  | 10 | 0 | -103 | 7658 | 82.4019 | T+132 sec | 40098.1039 | [12 empty] | 144.8783 | -118.6291 | 0.080002 | -103
T+134 sec | 40098.1039 | 59.917 | 3775.6355 |  |  | 3090 | 85.4902 | 84.2251 |  | 0.5823 | 3791.9763 | 3790.818 | 3797.7886 | 3712.2763 | 3693.0603 |  |  |  | T+134 sec | 40098.1039 | 59.917 | 3775.6355 | 335 | -228.9802 | 16 |  | 10 | 0 | -103 | 7659 | 85.4902 | T+134 sec | 40098.1039 | [12 empty] | 144.1554 | -115.2087 | 0.083 | -103
T+136 sec | 40098.1039 | 59.92 | 3774.6042 |  |  | 3090 | 82.4019 | 83.587 |  | 0.5823 | 3791.9205 | 3790.5831 | 3797.7036 | 3712.8586 | 3693.3514 |  |  |  | T+136 sec | 40098.1039 | 59.92 | 3774.6042 | 335 | -219.9756 | 16 |  | 10 | 0 | -103 | 7659 | 82.4019 | T+136 sec | 40098.1039 | [12 empty] | 143.1241 | -117.1928 | 0.080002 | -103
T+138 sec | 40098.104 | 59.921 | 3773.3337 |  |  | 3090 | 81.3685 | 82.8105 |  | 0.5823 | 3791.7263 | 3790.3366 | 3797.6182 | 3713.4409 | 3693.6426 |  |  |  | T+138 sec | 40098.104 | 59.921 | 3773.3337 | 335 | -219.9756 | 16 |  | 10 | 0 | -103 | 7659 | 81.3685 | T+138 sec | 40098.104 | [12 empty] | 141.8536 | -117.1146 | 0.078999 | -103
T+140 sec | 40098.104 | 59.923 | 3773.9578 |  |  | 3090 | 79.3097 | 81.5852 |  | 0.5823 | 3791.0833 | 3790.1059 | 3797.5261 | 3714.0232 | 3693.9337 |  |  |  | T+140 sec | 40098.104 | 59.923 | 3773.9578 | 335 | -219.9756 | 16 |  | 10 | 0 | -103 | 7660 | 79.3097 | T+140 sec | 40098.104 | [12 empty] | 142.4776 | -119.6036 | 0.077 | -103
T+142 sec | 40098.104 | 59.926 | 3772.7224 |  |  | 3090 | 76.2214 | 79.7079 |  | 0.5823 | 3789.7883 | 3789.8645 | 3797.4187 | 3714.6055 | 3694.2249 |  |  |  | T+142 sec | 40098.104 | 59.926 | 3772.7224 | 335 | -219.9756 | 16 |  | 10 | 0 | -103 | 7660 | 76.2214 | T+142 sec | 40098.104 | [12 empty] | 141.2423 | -121.6279 | 0.074001 | -103
T+144 sec | 40098.104 | 59.925 | 3771.6704 |  |  | 3090 | 77.2508 | 78.8479 |  | 0.5823 | 3789.5106 | 3789.6153 | 3797.3103 | 3715.1878 | 3694.516 |  |  |  | T+144 sec | 40098.104 | 59.925 | 3771.6704 | 335 | -219.9756 | 16 |  | 10 | 0 | -103 | 7661 | 77.2508 | T+144 sec | 40098.104 | [12 empty] | 140.1903 | -119.6919 | 0.075001 | -103
T+146 sec | 40098.1041 | 59.928 | 3769.6296 |  |  | 3090 | 74.1586 | 77.2066 |  | 0.5823 | 3788.4517 | 3789.3452 | 3797.1906 | 3715.7701 | 3694.8072 |  |  |  | T+146 sec | 40098.1041 | 59.928 | 3769.6296 | 335 | -229.0892 | 16 |  | 10 | 0 | -103 | 7661 | 74.1586 | T+146 sec | 40098.1041 | [12 empty] | 138.1495 | -121.0523 | 0.071999 | -103
T+148 sec | 40098.1041 | 59.927 | 3768.707 |  |  | 3090 | 75.1919 | 76.5015 |  | 0.5823 | 3788.3288 | 3789.07 | 3797.0725 | 3716.3524 | 3695.0983 |  |  |  | T+148 sec | 40098.1041 | 59.927 | 3768.707 | 335 | -229.0892 | 16 |  | 10 | 0 | -103 | 7662 | 75.1919 | T+148 sec | 40098.1041 | [12 empty] | 137.2269 | -119.196 | 0.073002 | -103
T+150 sec | 40098.1041 | 59.932 | 3767.6428 |  |  | 3090 | 70.0408 | 74.2402 |  | 0.5823 | 3786.6499 | 3788.7881 | 3796.9353 | 3716.9347 | 3695.3895 |  |  |  | T+150 sec | 40098.1041 | 59.932 | 3767.6428 | 335 | -229.0892 | 16 |  | 10 | 0 | -103 | 7662 | 70.0408 | T+150 sec | 40098.1041 | [12 empty] | 136.1627 | -123.6426 | 0.068001 | -103
T+152 sec | 40098.1041 | 59.927 | 3767.021 |  |  | 3090 | 75.1919 | 74.5733 |  | 0.5823 | 3787.5653 | 3788.5054 | 3796.8136 | 3717.517 | 3695.6806 |  |  |  | T+152 sec | 40098.1041 | 59.927 | 3767.021 | 335 | -229.0892 | 16 |  | 10 | 0 | -103 | 7663 | 75.1919 | T+152 sec | 40098.1041 | [12 empty] | 135.5409 | -117.7315 | 0.073002 | -103
T+154 sec | 40098.1041 | 59.928 | 3767.408 |  |  | 3090 | 74.1586 | 74.4282 |  | 0.5823 | 3788.0024 | 3788.2349 | 3796.7007 | 3718.0993 | 3695.9718 |  |  |  | T+154 sec | 40098.1041 | 59.928 | 3767.408 | 335 | -229.0892 | 16 |  | 10 | 0 | -103 | 7663 | 74.1586 | T+154 sec | 40098.1041 | [12 empty] | 135.9278 | -119.1056 | 0.071999 | -103
T+156 sec | 40098.1042 | 59.931 | 3766.7881 |  |  | 3090 | 71.0703 | 73.2529 |  | 0.5823 | 3787.4095 | 3787.9634 | 3796.5831 | 3718.6816 | 3696.2629 |  |  |  | T+156 sec | 40098.1042 | 59.931 | 3766.7881 | 335 | -229.6633 | 16 |  | 10 | 0 | -103 | 7664 | 71.0703 | T+156 sec | 40098.1042 | [12 empty] | 135.3079 | -121.7614 | 0.069 | -103
T+158 sec | 40098.1042 | 59.929 | 3766.259 |  |  | 3090 | 73.1291 | 73.2096 |  | 0.5823 | 3787.9484 | 3787.6921 | 3796.4751 | 3719.2639 | 3696.5541 |  |  |  | T+158 sec | 40098.1042 | 59.929 | 3766.259 | 335 | -229.6633 | 16 |  | 10 | 0 | -103 | 7664 | 73.1291 | T+158 sec | 40098.1042 | [12 empty] | 134.7789 | -119.1422 | 0.070999 | -103
T+160 sec | 40098.1042 | 59.931 | 3765.6716 |  |  | 3090 | 71.0703 | 72.4608 |  | 0.5823 | 3787.782 | 3787.4203 | 3796.3678 | 3719.8462 | 3696.8452 |  |  |  | T+160 sec | 40098.1042 | 59.931 | 3765.6716 | 335 | -229.6633 | 16 |  | 10 | 0 | -103 | 7665 | 71.0703 | T+160 sec | 40098.1042 | [12 empty] | 134.1915 | -120.7567 | 0.069 | -103
T+162 sec | 40098.1042 | 59.933 | 3766.1226 |  |  | 3090 | 69.0114 | 71.2535 |  | 0.5823 | 3787.157 | 3787.1605 | 3796.2555 | 3720.4285 | 3697.1364 |  |  |  | T+162 sec | 40098.1042 | 59.933 | 3766.1226 | 335 | -229.6633 | 16 |  | 10 | 0 | -103 | 7666 | 69.0114 | T+162 sec | 40098.1042 | [12 empty] | 134.6424 | -123.3819 | 0.067001 | -103
T+164 sec | 40098.1043 | 59.937 | 3764.2427 |  |  | 3090 | 64.8897 | 69.0262 |  | 0.5823 | 3785.512 | 3786.8844 | 3796.126 | 3721.0108 | 3697.4275 |  |  |  | T+164 sec | 40098.1043 | 59.937 | 3764.2427 | 335 | -229.6633 | 16 |  | 10 | 0 | -103 | 7666 | 64.8897 | T+164 sec | 40098.1043 | [12 empty] | 132.7625 | -126.2902 | 0.063 | -103
T+166 sec | 40098.1043 | 59.937 | 3765.105 |  |  | 3090 | 64.8897 | 67.5784 |  | 0.5823 | 3784.6465 | 3786.6251 | 3795.9894 | 3721.5931 | 3697.7187 |  |  |  | T+166 sec | 40098.1043 | 59.937 | 3765.105 | 335 | -229.2339 | 16 |  | 10 | 0 | -103 | 7667 | 64.8897 | T+166 sec | 40098.1043 | [12 empty] | 133.6248 | -127.1105 | 0.063 | -103
T+168 sec | 40098.1043 | 59.945 | 3762.9353 |  |  | 3090 | 56.6503 | 63.7536 |  | 0.5823 | 3781.404 | 3786.3464 | 3795.8178 | 3722.1754 | 3698.0098 |  |  |  | T+168 sec | 40098.1043 | 59.945 | 3762.9353 | 335 | -229.2339 | 16 |  | 10 | 0 | -103 | 7668 | 56.6503 | T+168 sec | 40098.1043 | [12 empty] | 131.4552 | -135.3456 | 0.055 | -103
T+170 sec | 40098.1043 | 59.949 | 3758.3872 |  |  | 3090 | 52.5286 | 59.8249 |  | 0.5823 | 3778.0575 | 3786.0213 | 3795.6113 | 3722.7577 | 3698.301 |  |  |  | T+170 sec | 40098.1043 | 59.949 | 3758.3872 | 335 | -229.2339 | 16 |  | 10 | 0 | -103 | 7668 | 52.5286 | T+170 sec | 40098.1043 | [12 empty] | 126.9071 | -136.2776 | 0.050999 | -103
T+172 sec | 40098.1044 | 59.947 | 3753.9224 |  |  | 3090 | 54.5914 | 57.9932 |  | 0.5823 | 3776.8081 | 3785.6524 | 3795.3952 | 3723.34 | 3698.5921 |  |  |  | T+172 sec | 40098.1044 | 59.947 | 3753.9224 | 335 | -229.2339 | 16 |  | 10 | 0 | -103 | 7669 | 54.5914 | T+172 sec | 40098.1044 | [12 empty] | 122.4422 | -128.715 | 0.053001 | -103
T+174 sec | 40098.1044 | 59.942 | 3749.8672 |  |  | 3090 | 59.7386 | 58.6041 |  | 0.5823 | 3778.0014 | 3785.2457 | 3795.1975 | 3723.9223 | 3698.8833 |  |  |  | T+174 sec | 40098.1044 | 59.942 | 3749.8672 | 350 | -229.2339 | 16 |  | 10 | 0 | -103 | 7669 | 59.7386 | T+174 sec | 40098.1044 | [12 empty] | 118.3871 | -118.2406 | 0.057999 | -103
T+176 sec | 40098.1044 | 59.941 | 3746.8887 |  |  | 3090 | 60.7681 | 59.3615 |  | 0.5823 | 3779.3411 | 3784.8148 | 3795.0193 | 3724.5046 | 3699.1744 |  |  |  | T+176 sec | 40098.1044 | 59.941 | 3746.8887 | 350 | -231.4099 | 16 |  | 10 | 0 | -103 | 7670 | 60.7681 | T+176 sec | 40098.1044 | [12 empty] | 115.4085 | -114.1265 | 0.058998 | -103
T+178 sec | 40098.1044 | 59.942 | 3747.8755 |  |  | 3090 | 59.7386 | 59.4935 |  | 0.5823 | 3780.0554 | 3784.4043 | 3794.8531 | 3725.0869 | 3699.4656 |  |  |  | T+178 sec | 40098.1044 | 59.942 | 3747.8755 | 350 | -231.4099 | 16 |  | 10 | 0 | -103 | 7670 | 59.7386 | T+178 sec | 40098.1044 | [12 empty] | 116.3954 | -116.2513 | 0.057999 | -103
T+180 sec | 40098.1044 | 59.945 | 3749.5933 |  |  | 3090 | 56.6503 | 58.4984 |  | 0.5823 | 3779.6426 | 3784.0218 | 3794.6859 | 3725.6692 | 3699.7567 |  |  |  | T+180 sec | 40098.1044 | 59.945 | 3749.5933 | 350 | -231.4099 | 16 |  | 10 | 0 | -103 | 7671 | 56.6503 | T+180 sec | 40098.1044 | [12 empty] | 118.1131 | -121.6087 | 0.055 | -103
| 40098.1045 | 59.948 | 3748.6611 |  |  | 3090 | 53.5581 | 56.7693 |  | 0.5823 | 3778.4958 | 3783.6374 | 3794.5099 | 3726.2515 | 3700.0479 |  |  |  |  | 40098.1045 | 59.948 | 3748.6611 | 350 | -231.4099 | 16 |  | 10 | 0 | -103 | 7671 | 53.5581 | [14 empty] | 117.181 | -124.4972 | 0.051998 | -103
| 40098.1045 | 59.947 | 3746.7061 |  |  | 3090 | 54.5914 | 56.007 |  | 0.5823 | 3778.3158 | 3783.2403 | 3794.3358 | 3726.8338 | 3700.3391 |  |  |  |  | 40098.1045 | 59.947 | 3746.7061 | 350 | -231.4099 | 16 |  | 10 | 0 | -103 | 7672 | 54.5914 | [14 empty] | 115.2259 | -121.129 | 0.053001 | -103
| 40098.1045 | 59.949 | 3749.0769 |  |  | 3090 | 52.5286 | 54.7896 |  | 0.5823 | 3777.6807 | 3782.8769 | 3794.1586 | 3727.4161 | 3700.6302 |  |  |  |  | 40098.1045 | 59.949 | 3749.0769 | 350 | -218.6223 | 16 |  | 10 | 0 | -103 | 7673 | 52.5286 | [14 empty] | 117.5968 | -126.2799 | 0.050999 | -103
| 40098.1045 | 59.951 | 3742.7415 |  |  | 3090 | 50.4698 | 53.2777 |  | 0.5823 | 3776.7511 | 3782.4544 | 3793.9754 | 3727.9984 | 3700.9214 |  |  |  |  | 40098.1045 | 59.951 | 3742.7415 | 350 | -218.6223 | 16 |  | 10 | 0 | -103 | 7673 | 50.4698 | [14 empty] | 111.2613 | -122.0975 | 0.049 | -103
| 40098.1046 | 59.952 | 3740.259 |  |  | 3090 | 49.4403 | 51.9346 |  | 0.5823 | 3775.9903 | 3782.0149 | 3793.788 | 3728.5807 | 3701.2125 |  |  |  |  | 40098.1046 | 59.952 | 3740.259 | 350 | -218.6223 | 16 |  | 10 | 0 | -103 | 7673 | 49.4403 | [14 empty] | 108.7789 | -120.6971 | 0.048 | -103
| 40098.1046 | 59.953 | 3736.1392 |  |  | 3090 | 48.4109 | 50.7013 |  | 0.5823 | 3775.3393 | 3781.5419 | 3793.5979 | 3729.163 | 3701.5037 |  |  |  |  | 40098.1046 | 59.953 | 3736.1392 | 350 | -218.6223 | 16 |  | 10 | 0 | -103 | 7673 | 48.4109 | [14 empty] | 104.659 | -117.428 | 0.047001 | -103
| 40098.1046 | 59.951 | 3731.3821 |  |  | 3090 | 50.4698 | 50.6203 |  | 0.5823 | 3775.8406 | 3781.0301 | 3793.4167 | 3729.7453 | 3701.7948 |  |  |  |  | 40098.1046 | 59.951 | 3731.3821 | 350 | -218.6223 | 16 |  | 10 | 0 | -103 | 7673 | 50.4698 | [14 empty] | 99.9019 | -109.6317 | 0.049 | -103
| 40098.1046 | 59.952 | 3727.8384 |  |  | 3090 | 49.4403 | 50.2073 |  | 0.5823 | 3776.0099 | 3780.4928 | 3793.2408 | 3730.3276 | 3702.086 |  |  |  |  | 40098.1046 | 59.952 | 3727.8384 | 350 | -213.5359 | 16 |  | 10 | 0 | -103 | 7673 | 49.4403 | [14 empty] | 96.3582 | -106.9156 | 0.048 | -103
| 40098.1047 | 59.952 | 3725.9517 |  |  | 3090 | 49.4403 | 49.9389 |  | 0.5823 | 3776.3238 | 3779.9474 | 3793.0717 | 3730.9099 | 3702.3771 |  |  |  |  | 40098.1047 | 59.952 | 3725.9517 | 350 | -213.5359 | 16 |  | 10 | 0 | -103 | 7673 | 49.4403 | [14 empty] | 94.4715 | -104.8221 | 0.048 | -103
| 40098.1047 | 59.952 | 3722.6489 |  |  | 3090 | 49.4403 | 49.7644 |  | 0.5823 | 3776.7316 | 3779.3801 | 3792.9099 | 3731.4922 | 3702.6683 |  |  |  |  | 40098.1047 | 59.952 | 3722.6489 | 350 | -213.5359 | 16 |  | 10 | 0 | -103 | 7673 | 49.4403 | [14 empty] | 91.1688 | -101.1575 | 0.048 | -103
| 40098.1047 | 59.955 | 3720.5781 |  |  | 3090 | 46.3481 | 48.5687 |  | 0.5823 | 3776.1182 | 3778.8036 | 3792.7453 | 3732.0745 | 3702.9594 |  |  |  |  | 40098.1047 | 59.955 | 3720.5781 | 350 | -213.5359 | 16 |  | 10 | 0 | -103 | 7673 | 46.3481 | [14 empty] | 89.098 | -102.2664 | 0.044998 | -103
| 40098.1047 | 59.952 | 3717.9961 |  |  | 3090 | 49.4403 | 48.8738 |  | 0.5823 | 3777.0056 | 3778.2132 | 3792.5924 | 3732.6568 | 3703.2506 |  |  |  |  | 40098.1047 | 59.952 | 3717.9961 | 350 | -213.5359 | 16 |  | 10 | 0 | -103 | 7673 | 49.4403 | [14 empty] | 86.516 | -95.9949 | 0.048 | -103
| 40098.1047 | 59.954 | 3718.1418 |  |  | 3090 | 47.3815 | 48.3515 |  | 0.5823 | 3777.0656 | 3777.6356 | 3792.4431 | 3733.2391 | 3703.5417 |  |  |  |  | 40098.1047 | 59.954 | 3718.1418 | 350 | -225.6519 | 16 |  | 10 | 0 | -103 | 7673 | 47.3815 | [14 empty] | 86.6617 | -98.3377 | 0.046001 | -103
| 40098.1048 | 59.952 | 3715.7527 |  |  | 3090 | 49.4403 | 48.7326 |  | 0.5823 | 3778.029 | 3777.0462 | 3792.3059 | 3733.8215 | 3703.8329 |  |  |  |  | 40098.1048 | 59.952 | 3715.7527 | 350 | -225.6519 | 16 |  | 10 | 0 | -103 | 7673 | 49.4403 | [14 empty] | 84.2725 | -93.5057 | 0.048 | -103
| 40098.1048 | 59.953 | 3713.6938 |  |  | 3090 | 48.4109 | 48.62 |  | 0.5823 | 3778.4987 | 3776.4486 | 3792.1756 | 3734.4038 | 3704.124 |  |  |  |  | 40098.1048 | 59.953 | 3713.6938 | 350 | -225.6519 | 16 |  | 10 | 0 | -103 | 7673 | 48.4109 | [14 empty] | 82.2137 | -92.2442 | 0.047001 | -103
| 40098.1048 | 59.953 | 3713.4836 |  |  | 3090 | 48.4109 | 48.5468 |  | 0.5823 | 3779.0078 | 3775.8601 | 3792.0525 | 3734.9861 | 3704.4152 |  |  |  |  | 40098.1048 | 59.953 | 3713.4836 | 350 | -225.6519 | 16 |  | 10 | 0 | -103 | 7673 | 48.4109 | [14 empty] | 82.0035 | -92.0084 | 0.047001 | -103
| 40098.1048 | 59.952 | 3710.8481 |  |  | 3090 | 49.4403 | 48.8596 |  | 0.5823 | 3779.9029 | 3775.2582 | 3791.94 | 3735.5684 | 3704.7063 |  |  |  |  | 40098.1048 | 59.952 | 3710.8481 | 350 | -225.6519 | 16 |  | 10 | 0 | -103 | 7673 | 49.4403 | [14 empty] | 79.368 | -88.0638 | 0.048 | -103
| 40098.1049 | 59.954 | 3710.8101 |  |  | 3090 | 47.3815 | 48.3422 |  | 0.5823 | 3779.9679 | 3774.6669 | 3791.8302 | 3736.1507 | 3704.9975 |  |  |  |  | 40098.1049 | 59.954 | 3710.8101 | 350 | -212.5736 | 16 |  | 10 | 0 | -103 | 7673 | 47.3815 | [14 empty] | 79.3299 | -90.0181 | 0.046001 | -103
| 40098.1049 | 59.954 | 3712.0918 |  |  | 3090 | 47.3815 | 48.006 |  | 0.5823 | 3780.2139 | 3774.098 | 3791.7246 | 3736.733 | 3705.2886 |  |  |  |  | 40098.1049 | 59.954 | 3712.0918 | 350 | -212.5736 | 16 |  | 10 | 0 | -103 | 7674 | 47.3815 | [14 empty] | 80.6117 | -91.4725 | 0.046001 | -103
| 40098.1049 | 59.959 | 3714.6226 |  |  | 3090 | 42.2304 | 45.9845 |  | 0.5823 | 3778.7748 | 3773.5622 | 3791.6079 | 3737.3153 | 3705.5798 |  |  |  |  | 40098.1049 | 59.959 | 3714.6226 | 350 | -212.5736 | 16 |  | 10 | 0 | -103 | 7675 | 42.2304 | [14 empty] | 83.1424 | -100.0202 | 0.041 | -103
| 40098.1049 | 59.957 | 3715.1296 |  |  | 3090 | 44.2892 | 45.3912 |  | 0.5823 | 3778.7637 | 3773.0405 | 3791.4933 | 3737.8976 | 3705.8709 |  |  |  |  | 40098.1049 | 59.957 | 3715.1296 | 350 | -212.5736 | 16 |  | 10 | 0 | -103 | 7676 | 44.2892 | [14 empty] | 83.6495 | -98.2673 | 0.042999 | -103
| 40098.105 | 59.956 | 3716.1682 |  |  | 3090 | 45.3187 | 45.3658 |  | 0.5823 | 3779.3206 | 3772.5372 | 3791.3855 | 3738.4799 | 3706.1621 |  |  |  |  | 40098.105 | 59.956 | 3716.1682 | 350 | -212.5736 | 16 |  | 10 | 0 | -103 | 7677 | 45.3187 | [14 empty] | 84.6881 | -98.3328 | 0.043999 | -103
| 40098.105 | 59.954 | 3716.4614 |  |  | 3090 | 47.3815 | 46.0713 |  | 0.5823 | 3780.6084 | 3772.0453 | 3791.291 | 3739.0622 | 3706.4532 |  |  |  |  | 40098.105 | 59.954 | 3716.4614 | 350 | -219.8973 | 16 |  | 10 | 0 | -103 | 7678 | 47.3815 | [14 empty] | 84.9813 | -96.4309 | 0.046001 | -103
| 40098.105 | 59.956 | 3716.98 |  |  | 3090 | 45.3187 | 45.8079 |  | 0.5823 | 3780.9273 | 3771.5665 | 3791.2009 | 3739.6445 | 3706.7444 |  |  |  |  | 40098.105 | 59.956 | 3716.98 | 350 | -219.8973 | 16 |  | 10 | 0 | -103 | 7679 | 45.3187 | [14 empty] | 85.4998 | -99.2753 | 0.043999 | -103
| 40098.105 | 59.955 | 3717.759 |  |  | 3090 | 46.3481 | 45.997 |  | 0.5823 | 3781.6987 | 3771.1026 | 3791.119 | 3740.2268 | 3707.0355 |  |  |  |  | 40098.105 | 59.955 | 3717.759 | 350 | -219.8973 | 16 |  | 10 | 0 | -103 | 7680 | 46.3481 | [14 empty] | 86.2789 | -99.0307 | 0.044998 | -103
| 40098.105 | 59.958 | 3722.3613 |  |  | 3090 | 43.2598 | 45.039 |  | 0.5823 | 3781.323 | 3770.686 | 3791.0352 | 3740.8091 | 3707.3267 |  |  |  |  | 40098.105 | 59.958 | 3722.3613 | 350 | -219.8973 | 16 |  | 10 | 0 | -103 | 7681 | 43.2598 | [14 empty] | 90.8812 | -108.0311 | 0.042 | -103
| 40098.1051 | 59.961 | 3721.9731 |  |  | 3090 | 40.1715 | 43.3353 |  | 0.5823 | 3780.2017 | 3770.2732 | 3790.9434 | 3741.3914 | 3707.6178 |  |  |  |  | 40098.1051 | 59.961 | 3721.9731 | 350 | -219.8973 | 16 |  | 10 | 0 | -103 | 7682 | 40.1715 | [14 empty] | 90.493 | -111.5453 | 0.039001 | -103
| 40098.1051 | 59.962 | 3722.658 |  |  | 3090 | 39.1381 | 41.8663 |  | 0.5823 | 3779.315 | 3769.8731 | 3790.8457 | 3741.9737 | 3707.909 |  |  |  |  | 40098.1051 | 59.962 | 3722.658 | 350 | -231.1754 | 16 |  | 10 | 0 | -103 | 7684 | 39.1381 | [14 empty] | 91.1778 | -113.7967 | 0.037998 | -103
| 40098.1051 | 59.962 | 3722.2666 |  |  | 3090 | 39.1381 | 40.9115 |  | 0.5823 | 3778.9424 | 3769.4764 | 3790.7465 | 3742.556 | 3708.2001 |  |  |  |  | 40098.1051 | 59.962 | 3722.2666 | 350 | -231.1754 | 16 |  | 10 | 0 | -103 | 7685 | 39.1381 | [14 empty] | 90.7865 | -113.3083 | 0.037998 | -103
| 40098.1051 | 59.968 | 3722.2776 |  |  | 3090 | 32.9615 | 38.129 |  | 0.5823 | 3776.7423 | 3769.0863 | 3790.6308 | 3743.1383 | 3708.4913 |  |  |  |  | 40098.1051 | 59.968 | 3722.2776 | 350 | -231.1754 | 16 |  | 10 | 0 | -103 | 7687 | 32.9615 | [14 empty] | 90.7975 | -122.4895 | 0.032001
| 40098.1052 | 59.966 | 3721.7866 |  |  | 3090 | 35.0204 | 37.041 |  | 0.5823 | 3776.2366 | 3768.6986 | 3790.5128 | 3743.7206 | 3708.7824 |  |  |  |  | 40098.1052 | 59.966 | 3721.7866 | 350 | -231.1754 | 16 |  | 10 | 0 | -103 | 7689 | 35.0204 | [14 empty] | 90.3065 | -118.6282 | 0.034
| 40098.1052 | 59.966 | 3723.0908 |  |  | 3090 | 35.0204 | 36.3338 |  | 0.5823 | 3776.1117 | 3768.3278 | 3790.3957 | 3744.3029 | 3709.0736 |  |  |  |  | 40098.1052 | 59.966 | 3723.0908 | 350 | -231.1754 | 16 |  | 10 | 0 | -103 | 7690 | 35.0204 | [14 empty] | 91.6107 | -120.3415 | 0.034
| 40098.1052 | 59.968 | 3723.9839 |  |  | 3090 | 32.9615 | 35.1535 |  | 0.5823 | 3775.5137 | 3767.9702 | 3790.2757 | 3744.8852 | 3709.3647 |  |  |  |  | 40098.1052 | 59.968 | 3723.9839 | 350 | -226.6341 | 16 |  | 10 | 0 | -103 | 7692 | 32.9615 | [14 empty] | 92.5038 | -124.7914 | 0.032001
| 40098.1052 | 59.97 | 3723.4346 |  |  | 3090 | 30.8987 | 33.6643 |  | 0.5823 | 3774.6068 | 3767.6139 | 3790.1504 | 3745.4675 | 3709.6559 |  |  |  |  | 40098.1052 | 59.97 | 3723.4346 | 350 | -226.6341 | 16 |  | 10 | 0 | -103 | 7692 | 30.8987 | [14 empty] | 91.9544 | -127.4949 | 0.029999
| 40098.1053 | 59.974 | 3723.8931 |  |  | 3090 | 26.781 | 31.2552 |  | 0.5823 | 3772.78 | 3767.2669 | 3790.0125 | 3746.0498 | 3709.947 |  |  |  |  | 40098.1053 | 59.974 | 3723.8931 | 350 | -226.6341 | 16 |  | 10 | 0 | -103 | 7693 | 26.781 | [14 empty] | 92.4129 | -135.6496 | 0.026001
| 40098.1053 | 59.97 | 3725.4028 |  |  | 3090 | 30.8987 | 31.1304 |  | 0.5823 | 3773.2375 | 3766.9373 | 3789.8804 | 3746.6321 | 3710.2382 |  |  |  |  | 40098.1053 | 59.97 | 3725.4028 | 350 | -226.6341 | 16 |  | 10 | 0 | -103 | 7693 | 30.8987 | [14 empty] | 93.9227 | -130.2239 | 0.029999
| 40098.1053 | 59.969 | 3727.1211 |  |  | 3090 | 31.9282 | 31.4096 |  | 0.5823 | 3774.099 | 3766.6262 | 3789.7571 | 3747.2144 | 3710.5293 |  |  |  |  | 40098.1053 | 59.969 | 3727.1211 | 350 | -226.6341 | 16 |  | 10 | 0 | -103 | 7694 | 31.9282 | [14 empty] | 95.641 | -130.7938 | 0.030998
| 40098.1053 | 59.969 | 3728.053 |  |  | 3090 | 31.9282 | 31.5911 |  | 0.5823 | 3774.8628 | 3766.3272 | 3789.6417 | 3747.7967 | 3710.8205 |  |  |  |  | 40098.1053 | 59.969 | 3728.053 | 350 | -227.2551 | 16 |  | 10 | 0 | -103 | 7694 | 31.9282 | [14 empty] | 96.5728 | -132.0682 | 0.030998
| 40098.1053 | 59.97 | 3731.1299 |  |  | 3090 | 30.8987 | 31.3488 |  | 0.5823 | 3775.2028 | 3766.0564 | 3789.5306 | 3748.379 | 3711.1116 |  |  |  |  | 40098.1053 | 59.97 | 3731.1299 | 350 | -227.2551 | 16 |  | 10 | 0 | -103 | 7695 | 30.8987 | [14 empty] | 99.6497 | -138.1645 | 0.029999
| 40098.1054 | 59.971 | 3732.53 |  |  | 3090 | 29.8693 | 30.831 |  | 0.5823 | 3775.2673 | 3765.8005 | 3789.4217 | 3748.9613 | 3711.4028 |  |  |  |  | 40098.1054 | 59.971 | 3732.53 | 350 | -227.2551 | 16 |  | 10 | 0 | -103 | 7695 | 29.8693 | [14 empty] | 101.0499 | -142.0746 | 0.028999
| 40098.1054 | 59.973 | 3733.3271 |  |  | 3090 | 27.8104 | 29.7738 |  | 0.5823 | 3774.7924 | 3765.5545 | 3789.3109 | 3749.5436 | 3711.694 |  |  |  |  | 40098.1054 | 59.973 | 3733.3271 | 350 | -227.2551 | 16 |  | 10 | 0 | -103 | 7695 | 27.8104 | [14 empty] | 101.847 | -147.3361 | 0.027
| 40098.1054 | 59.973 | 3736.5352 |  |  | 3090 | 27.8104 | 29.0866 |  | 0.5823 | 3774.6875 | 3765.3363 | 3789.2009 | 3750.1259 | 3711.9851 |  |  |  |  | 40098.1054 | 59.973 | 3736.5352 | 350 | -227.2551 | 16 |  | 10 | 0 | -103 | 7696 | 27.8104 | [14 empty] | 105.055 | -151.9769 | 0.027
| 40098.1054 | 59.976 | 3736.9075 |  |  | 3090 | 24.7182 | 27.5577 |  | 0.5823 | 3773.7409 | 3765.1241 | 3789.0856 | 3750.7082 | 3712.2763 |  |  |  |  | 40098.1054 | 59.976 | 3736.9075 | 350 | -229.2902 | 16 |  | 10 | 0 | -103 | 7696 | 24.7182 | [14 empty] | 105.4273 | -159.4401 | 0.023998
| 40098.1055 | 59.978 | 3736.8218 |  |  | 3090 | 22.6593 | 25.8433 |  | 0.5823 | 3772.6088 | 3764.9145 | 3788.9635 | 3751.2905 | 3712.5674 |  |  |  |  | 40098.1055 | 59.978 | 3736.8218 | 350 | -229.2902 | 16 |  | 10 | 0 | -103 | 7697 | 22.6593 | [14 empty] | 105.3416 | -164.2765 | 0.021999
| 40098.1055 | 59.978 | 3738.6992 |  |  | 3090 | 22.6593 | 24.7289 |  | 0.5823 | 3772.0767 | 3764.7217 | 3788.8393 | 3751.8728 | 3712.8586 |  |  |  |  | 40098.1055 | 59.978 | 3738.6992 | 350 | -229.2902 | 16 |  | 10 | 0 | -103 | 7697 | 22.6593 | [14 empty] | 107.2191 | -167.2043 | 0.021999
| 40098.1055 | 59.976 | 3739.9438 |  |  | 3090 | 24.7182 | 24.7251 |  | 0.5823 | 3772.6553 | 3764.5409 | 3788.7212 | 3752.4551 | 3713.1497 |  |  |  |  | 40098.1055 | 59.976 | 3739.9438 | 350 | -229.2902 | 16 |  | 10 | 0 | -103 | 7697 | 24.7182 | [14 empty] | 108.4637 | -164.0321 | 0.023998
| 40098.1055 | 59.978 | 3740.877 |  |  | 3090 | 22.6593 | 24.0021 |  | 0.5823 | 3772.5145 | 3764.3694 | 3788.6038 | 3753.0374 | 3713.4409 |  |  |  |  | 40098.1055 | 59.978 | 3740.877 | 350 | -229.2902 | 16 |  | 10 | 0 | -103 | 7698 | 22.6593 | [14 empty] | 109.3968 | -170.6004 | 0.021999
| 40098.1056 | 59.976 | 3741.7937 |  |  | 3090 | 24.7182 | 24.2527 |  | 0.5823 | 3773.3475 | 3764.207 | 3788.494 | 3753.6197 | 3713.732 |  |  |  |  | 40098.1056 | 59.976 | 3741.7937 | 350 | -221.4614 | 16 |  | 10 | 0 | -103 | 7698 | 24.7182 | [14 empty] | 110.3136 | -166.8296 | 0.023998
| 40098.1056 | 59.978 | 3745.2336 |  |  | 3090 | 22.6593 | 23.6951 |  | 0.5823 | 3773.3721 | 3764.0715 | 3788.386 | 3754.202 | 3714.0232 |  |  |  |  | 40098.1056 | 59.978 | 3745.2336 | 350 | -221.4614 | 16 |  | 10 | 0 | -103 | 7698.33 | 22.6593 | [14 empty] | 113.7535 | -177.3945 | 0.021999
| 40098.1056 | 59.977 | 3746.6079 |  |  | 3090 | 23.6888 | 23.6929 |  | 0.5823 | 3773.9522 | 3763.9476 | 3788.2836 | 3754.7843 | 3714.3143 |  |  |  |  | 40098.1056 | 59.977 | 3746.6079 | 350 | -221.4614 | 16 |  | 10 | 0 | -103 | 7698.66 | 23.6888 | [14 empty] | 115.1278 | -176.7823 | 0.022999
| 40098.1056 | 59.98 | 3748.2998 |  |  | 3090 | 20.6005 | 22.6105 |  | 0.5823 | 3773.4521 | 3763.8374 | 3788.1792 | 3755.3666 | 3714.6055 |  |  |  |  | 40098.1056 | 59.98 | 3748.2998 | 350 | -221.4614 | 16 |  | 10 | 0 | -103 | 7698.99 | 20.6005 | [14 empty] | 116.8197 | -188.0376 | 0.02
| 40098.1056 | 59.982 | 3750.7163 |  |  | 3090 | 18.5416 | 21.1864 |  | 0.5823 | 3772.6103 | 3763.7457 | 3788.0703 | 3755.9489 | 3714.8966 |  |  |  |  | 40098.1056 | 59.982 | 3750.7163 | 350 | -221.4614 | 16 |  | 10 | 0 | -103 | 7699.32 | 18.5416 | [14 empty] | 119.2362 | -198.3079 | 0.018002
| 40098.1057 | 59.981 | 3751.5576 |  |  | 3090 | 19.571 | 20.621 |  | 0.5823 | 3772.6273 | 3763.661 | 3787.9631 | 3756.5313 | 3715.1878 |  |  |  |  | 40098.1057 | 59.981 | 3751.5576 | 350 | -241.2744 | 16 |  | 10 | 0 | -103 | 7699.65 | 19.571 | [14 empty] | 120.0775 | -196.4418 | 0.019001
| 40098.1057 | 59.98 | 3752.7476 |  |  | 3090 | 20.6005 | 20.6138 |  | 0.5823 | 3773.2024 | 3763.5858 | 3787.8613 | 3757.1136 | 3715.4789 |  |  |  |  | 40098.1057 | 59.98 | 3752.7476 | 350 | -241.2744 | 16 |  | 10 | 0 | -103 | 7699.98 | 20.6005 | [14 empty] | 121.2674 | -195.1969 | 0.02
| 40098.1057 | 59.979 | 3755.5986 |  |  | 3090 | 21.6299 | 20.9695 |  | 0.5823 | 3774.1403 | 3763.531 | 3787.7673 | 3757.6959 | 3715.7701 |  |  |  |  | 40098.1057 | 59.979 | 3755.5986 | 350 | -241.2744 | 16 |  | 10 | 0 | -103 | 7700.31 | 21.6299 | [14 empty] | 124.1185 | -196.6229 | 0.021
| 40098.1057 | 59.98 | 3756.4072 |  |  | 3090 | 20.6005 | 20.8403 |  | 0.5823 | 3774.5934 | 3763.4826 | 3787.6777 | 3758.2782 | 3716.0612 |  |  |  |  | 40098.1057 | 59.98 | 3756.4072 | 350 | -241.2744 | 16 |  | 10 | 0 | -103 | 7700.64 | 20.6005 | [14 empty] | 124.9271 | -201.0877 | 0.02
| 40098.1058 | 59.979 | 3756.9753 |  |  | 3090 | 21.6299 | 21.1167 |  | 0.5823 | 3775.4521 | 3763.4386 | 3787.5951 | 3758.8605 | 3716.3524 |  |  |  |  | 40098.1058 | 59.979 | 3756.9753 | 350 | -241.2744 | 16 |  | 10 | 0 | -103 | 7700.97 | 21.6299 | [14 empty] | 125.4952 | -198.8039 | 0.021
| 40098.1058 | 59.983 | 3760.4053 |  |  | 3090 | 17.5082 | 19.8537 |  | 0.5823 | 3774.7715 | 3763.4183 | 3787.509 | 3759.4428 | 3716.6435 |  |  |  |  | 40098.1058 | 59.983 | 3760.4053 | 350 | -243.0719 | 16 |  | 10 | 0 | -103 | 7701.3 | 17.5082 | [14 empty] | 128.9251 | -218.0607 | 0.016998
| 40098.1058 | 59.983 | 3760.9822 |  |  | 3090 | 17.5082 | 19.0328 |  | 0.5823 | 3774.5328 | 3763.402 | 3787.4225 | 3760.0251 | 3716.9347 |  |  |  |  | 40098.1058 | 59.983 | 3760.9822 | 350 | -243.0719 | 16 |  | 10 | 0 | -103 | 7701.63 | 17.5082 | [14 empty] | 129.502 | -219.0364 | 0.016998
| 40098.1058 | 59.984 | 3761.407 |  |  | 3090 | 16.4788 | 18.1389 |  | 0.5823 | 3774.2212 | 3763.3888 | 3787.3351 | 3760.6074 | 3717.2258 |  |  |  |  | 40098.1058 | 59.984 | 3761.407 | 350 | -243.0719 | 16 |  | 10 | 0 | -103 | 7701.96 | 16.4788 | [14 empty] | 129.9268 | -223.5337 | 0.015999
| 40098.1059 | 59.988 | 3762.7373 |  |  | 3090 | 12.3611 | 16.1167 |  | 0.5823 | 3772.7813 | 3763.3845 | 3787.2393 | 3761.1897 | 3717.517 |  |  |  |  | 40098.1059 | 59.988 | 3762.7373 | 350 | -243.0719 | 16 |  | 10 | 0 | -103 | 7702.29 | 12.3611 | [14 empty] | 131.2572 | -242.5018 | 0.012001
| 40098.1059 | 59.989 | 3763.2122 |  |  | 3090 | 11.3316 | 14.4419 |  | 0.5823 | 3771.6889 | 3763.3834 | 3787.1377 | 3761.772 | 3717.8081 |  |  |  |  | 40098.1059 | 59.989 | 3763.2122 | 350 | -243.0719 | 16 |  | 10 | 0 | -103 | 7702.62 | 11.3316 | [14 empty] | 131.732 | -247.9577 | 0.011002
| 40098.1059 | 59.987 | 3764.9575 |  |  | 3090 | 13.3905 | 14.0739 |  | 0.5823 | 3771.9032 | 3763.3936 | 3787.0388 | 3762.3543 | 3718.0993 |  |  |  |  | 40098.1059 | 59.987 | 3764.9575 | 350 | -241.6702 | 16 |  | 10 | 0 | -103 | 7702.95 | 13.3905 | [14 empty] | 133.4774 | -242.1327 | 0.013
| 40098.1059 | 59.987 | 3766.0852 |  |  | 3090 | 13.3905 | 13.8347 |  | 0.5823 | 3772.2463 | 3763.411 | 3786.9433 | 3762.9366 | 3718.3904 |  |  |  |  | 40098.1059 | 59.987 | 3766.0852 | 350 | -241.6702 | 16 |  | 10 | 0 | -103 | 7703.28 | 13.3905 | [14 empty] | 134.6051 | -244.1784 | 0.013
| 40098.1059 | 59.991 | 3766.4331 |  |  | 3090 | 9.2688 | 12.2367 |  | 0.5823 | 3771.2305 | 3763.4304 | 3786.8426 | 3763.5189 | 3718.6816 |  |  |  |  | 40098.1059 | 59.991 | 3766.4331 | 350 | -241.6702 | 16 |  | 10 | 0 | -103 | 7703.61 | 9.2688 | [14 empty] | 134.953 | -263.9714 | 0.0089989
| 40098.106 | 59.993 | 3767.251 |  |  | 3090 | 7.21 | 10.4773 |  | 0.5823 | 3770.0535 | 3763.4547 | 3786.7357 | 3764.1012 | 3718.9727 |  |  |  |  | 40098.106 | 59.993 | 3767.251 | 350 | -241.6702 | 16 |  | 10 | 0 | -103 | 7703.94 | 7.21 | [14 empty] | 135.7708 | -276.3772 | 0.007
| 40098.106 | 59.992 | 3767.7925 |  |  | 3090 | 8.2394 | 9.694 |  | 0.5823 | 3769.8525 | 3763.4821 | 3786.6288 | 3764.6835 | 3719.2639 |  |  |  |  | 40098.106 | 59.992 | 3767.7925 | 350 | -241.6702 | 16 |  | 10 | 0 | -103 | 7704.27 | 8.2394 | [14 empty] | 136.3123 | -271.9468 | 0.0079994
| 40098.106 | 59.991 | 3768.6335 |  |  | 3090 | 9.2688 | 9.5452 |  | 0.5823 | 3770.286 | 3763.5145 | 3786.526 | 3765.2658 | 3719.555 |  |  |  |  | 40098.106 | 59.991 | 3768.6335 | 350 | -228.1493 | 16 |  | 10 | 0 | -103 | 7704.6 | 9.2688 | [14 empty] | 137.1534 | -268.2755 | 0.0089989
| 40098.106 | 59.989 | 3771.1465 |  |  | 3090 | 11.3316 | 10.1705 |  | 0.5823 | 3771.4935 | 3763.5622 | 3786.4321 | 3765.8481 | 3719.8462 |  |  |  |  | 40098.106 | 59.989 | 3771.1465 | 350 | -228.1493 | 16 |  | 10 | 0 | -103 | 7704.93 | 11.3316 | [14 empty] | 139.6663 | -262.8924 | 0.011002
| 40098.1061 | 59.986 | 3772.4446 |  |  | 3090 | 14.4199 | 11.6578 |  | 0.5823 | 3773.5632 | 3763.6174 | 3786.3521 | 3766.4304 | 3720.1373 |  |  |  |  | 40098.1061 | 59.986 | 3772.4446 | 350 | -228.1493 | 16 |  | 10 | 0 | -103 | 7705.26 | 14.4199 | [14 empty] | 140.9644 | -251.1609 | 0.014
| 40098.1061 | 59.983 | 3773.6948 |  |  | 3090 | 17.5082 | 13.7054 |  | 0.5823 | 3776.1931 | 3763.6796 | 3786.2894 | 3767.0127 | 3720.4285 |  |  |  |  | 40098.1061 | 59.983 | 3773.6948 | 350 | -228.1493 | 16 |  | 10 | 0 | -103 | 7705.59 | 17.5082 | [14 empty] | 142.2147 | -240.5383 | 0.016998
| 40098.1061 | 59.983 | 3774.6685 |  |  | 3090 | 17.5082 | 15.0364 |  | 0.5823 | 3778.1064 | 3763.747 | 3786.2392 | 3767.595 | 3720.7196 |  |  |  |  | 40098.1061 | 59.983 | 3774.6685 | 350 | -228.1493 | 16 |  | 10 | 0 | -103 | 7705.92 | 17.5082 | [14 empty] | 143.1883 | -242.1851 | 0.016998
| 40098.1061 | 59.988 | 3775.8408 |  |  | 3090 | 12.3611 | 14.1 |  | 0.5823 | 3777.7523 | 3763.8208 | 3786.1875 | 3768.1773 | 3721.0108 |  |  |  |  | 40098.1061 | 59.988 | 3775.8408 | 350 | -235.129 | 16 |  | 10 | 0 | -103 | 7706.25 | 12.3611 | [14 empty] | 144.3607 | -266.711 | 0.012001
| 40098.1062 | 59.993 | 3775.3633 |  |  | 3090 | 7.21 | 11.6885 |  | 0.5823 | 3775.9231 | 3763.8907 | 3786.1253 | 3768.7596 | 3721.3019 |  |  |  |  | 40098.1062 | 59.993 | 3775.3633 | 350 | -235.129 | 16 |  | 10 | 0 | -103 | 7706.58 | 7.21 | [14 empty] | 143.8831 | -292.8907 | 0.007
| 40098.1062 | 59.996 | 3774.8662 |  |  | 3090 | 4.1217 | 9.0401 |  | 0.5823 | 3773.857 | 3763.9568 | 3786.0514 | 3769.3419 | 3721.5931 |  |  |  |  | 40098.1062 | 59.996 | 3774.8662 | 350 | -235.129 | 16 |  | 10 | 0 | -103 | 7706.91 | 4.1217 | [14 empty] | 143.3861 | -310.8517 | 0.0040016
| 40098.1062 | 59.998 | 3775.4917 |  |  | 3090 | 2.0589 | 6.5967 |  | 0.5823 | 3771.9959 | 3764.0259 | 3785.9672 | 3769.9242 | 3721.8842 |  |  |  |  | 40098.1062 | 59.998 | 3775.4917 | 350 | -235.129 | 16 |  | 10 | 0 | -103 | 7707.24 | 2.0589 | [14 empty] | 144.0116 | -326.3783 | 0.0019989
| 40098.1062 | 59.999 | 3776.4202 |  |  | 3090 | 1.0294 | 4.6481 |  | 0.5823 | 3770.6296 | 3764.0997 | 3785.8759 | 3770.5065 | 3722.1754 |  |  |  |  | 40098.1062 | 59.999 | 3776.4202 | 350 | -235.129 | 16 |  | 10 | 0 | -103 | 7707.57 | 1.0294 | [14 empty] | 144.94 | -336.0953 | 0.00099945
| 40098.1062 | 60.001 | 3778.5537 |  |  | 3090 | -1.0294 | 2.661 |  | 0 | 3768.6425 | 3764.1852 | 3785.7739 | 3770.5065 | 3722.4631 |  |  |  |  | 40098.1062 | 60.001 | 3778.5537 | 350 | -246.4331 | 16 |  | 10 | 0 | -103 | 7707.9 | -1.0294 | [14 empty] | 146.4913 |  | 0.00099945
| 40098.1063 | 59.999 | 3779.6919 |  |  | 3090 | 1.0294 | 2.0899 |  | 0 | 3768.0714 | 3764.2764 | 3785.6698 | 3770.5065 | 3722.7474 |  |  |  |  | 40098.1063 | 59.999 | 3779.6919 | 350 | -246.4331 | 16 |  | 10 | 0 | -103 | 7708.23 | 1.0294 | [14 empty] | 147.6295 |  | 0.00099945
| 40098.1063 | 59.999 | 3781.2559 |  |  | 3090 | 1.0294 | 1.7188 |  | 0 | 3767.7003 | 3764.3757 | 3785.5647 | 3770.5065 | 3723.0283 |  |  |  |  | 40098.1063 | 59.999 | 3781.2559 | 350 | -246.4331 | 16 |  | 10 | 0 | -103 | 7708.56 | 1.0294 | [14 empty] | 149.1934 |  | 0.00099945
| 40098.1063 | 59.999 | 3780.595 |  |  | 3090 | 1.0294 | 1.4775 |  | 0 | 3767.459 | 3764.47 | 3785.4594 | 3770.5065 | 3723.306 |  |  |  |  | 40098.1063 | 59.999 | 3780.595 | 350 | -246.4331 | 16 |  | 10 | 0 | -103 | 7708.89 | 1.0294 | [14 empty] | 148.5325 |  | 0.00099945
| 40098.1063 | 60.002 | 3783.092 |  |  | 3090 | -2.0589 | 0.23977 |  | 0 | 3766.2213 | 3764.5777 | 3785.3482 | 3770.5065 | 3723.5804 |  |  |  |  | 40098.1063 | 60.002 | 3783.092 | 350 | -246.4331 | 16 |  | 10 | 0 | -103 | 7709.22 | -2.0589 | [14 empty] | 151.0296 |  | 0.0019989
| 40098.1064 | 60.005 | 3783.8955 |  |  | 3090 | -5.1511 | -1.647 |  | 0 | 3764.3345 | 3764.6887 | 3785.2275 | 3770.5065 | 3723.8516 |  |  |  |  | 40098.1064 | 60.005 | 3783.8955 | 350 | -236.5535 | 16 |  | 10 | 0 | -103 | 7709.55 | -5.1511 | [14 empty] | 151.8331 |  | 0.0050011
| 40098.1064 | 60.007 | 3784.4209 |  |  | 3090 | -7.21 | -3.5941 |  | 0 | 3762.3874 | 3764.8014 | 3785.097 | 3770.5065 | 3724.1198 |  |  |  |  | 40098.1064 | 60.007 | 3784.4209 | 350 | -236.5535 | 16 |  | 10 | 0 | -103 | 7709.88 | -7.21 | [14 empty] | 152.3585 |  | 0.007
| 40098.1064 | 60.008 | 3785.7681 |  |  | 3090 | -8.2394 | -5.2199 |  | 0 | 3760.7616 | 3764.9206 | 3784.9587 | 3770.5065 | 3724.3848 |  |  |  |  | 40098.1064 | 60.008 | 3785.7681 | 350 | -236.5535 | 16 |  | 10 | 0 | -103 | 7710.21 | -8.2394 | [14 empty] | 153.7056 |  | 0.0079994
| 40098.1064 | 60.011 | 3785.4626 |  |  | 3090 | -11.3316 | -7.359 |  | 0 | 3758.6225 | 3765.0366 | 3784.8099 | 3770.5065 | 3724.6469 |  |  |  |  | 40098.1064 | 60.011 | 3785.4626 | 350 | -236.5535 | 16 |  | 10 | 0 | -103 | 7710.54 | -11.3316 | [14 empty] | 153.4002 |  | 0.011002
| 40098.1065 | 60.014 | 3786.8503 |  |  | 3090 | -14.4199 | -9.8303 |  | 0 | 3756.1511 | 3765.1592 | 3784.6489 | 3770.5065 | 3724.906 |  |  |  |  | 40098.1065 | 60.014 | 3786.8503 | 350 | -236.5535 | 16 |  | 10 | 0 | -103 | 7710.87 | -14.4199 | [14 empty] | 154.7879 |  | 0.014
| 40098.1065 | 60.017 | 3786.3042 |  |  | 3090 | -17.5082 | -12.5176 |  | 0 | 3753.4639 | 3765.2773 | 3784.4747 | 3770.5065 | 3725.1622 |  |  |  |  | 40098.1065 | 60.017 | 3786.3042 | 350 | -230.2976 | 16 |  | 10 | 0 | -103 | 7711.2 | -17.5082 | [14 empty] | 154.2418 |  | 0.016998
| 40098.1065 | 60.019 | 3787.2593 |  |  | 3090 | -19.571 | -14.9863 |  | 0 | 3750.9952 | 3765.3994 | 3784.2887 | 3770.5065 | 3725.4155 |  |  |  |  | 40098.1065 | 60.019 | 3787.2593 | 350 | -230.2976 | 16 |  | 10 | 0 | -103 | 7711.53 | -19.571 | [14 empty] | 155.1968 |  | 0.019001
| 40098.1065 | 60.021 | 3787.5159 |  |  | 3090 | -21.6299 | -17.3116 |  | 0 | 3748.6699 | 3765.5216 | 3784.0919 | 3770.5065 | 3725.666 |  |  |  |  | 40098.1065 | 60.021 | 3787.5159 | 350 | -230.2976 | 16 |  | 10 | 0 | -103 | 7711.86 | -21.6299 | [14 empty] | 155.4534 |  | 0.021
| 40098.1066 | 60.017 | 3787.9551 |  |  | 3090 | -17.5082 | -17.3804 |  | 0 | 3748.6011 | 3765.6449 | 3783.8969 | 3770.5065 | 3725.9137 |  |  |  |  | 40098.1066 | 60.017 | 3787.9551 | 350 | -230.2976 | 16 |  | 10 | 0 | -103 | 7712.19 | -17.5082 | [14 empty] | 155.8926 |  | 0.016998
| 40098.1066 | 60.017 | 3788.0303 |  |  | 3090 | -17.5082 | -17.4251 |  | 0 | 3748.5563 | 3765.7672 | 3783.7038 | 3770.5065 | 3726.1587 |  |  |  |  | 40098.1066 | 60.017 | 3788.0303 | 350 | -230.2976 | 16 |  | 10 | 0 | -103 | 7712.52 | -17.5082 | [14 empty] | 155.9678 |  | 0.016998
| 40098.1066 | 60.019 | 3788.6067 |  |  | 3090 | -19.571 | -18.1762 |  | 0 | 3747.8053 | 3765.8913 | 3783.5087 | 3770.5065 | 3726.4011 |  |  |  |  | 40098.1066 | 60.019 | 3788.6067 | 350 | -231.1755 | 16 |  | 10 | 0 | -103 | 7712.85 | -19.571 | [14 empty] | 156.5443 |  | 0.019001
| 40098.1066 | 60.023 | 3789.2158 |  |  | 3090 | -23.6888 | -20.1056 |  | 0 | 3745.8759 | 3766.0174 | 3783.3052 | 3770.5065 | 3726.6408 |  |  |  |  | 40098.1066 | 60.023 | 3789.2158 | 350 | -231.1755 | 16 |  | 10 | 0 | -103 | 7713.18 | -23.6888 | [14 empty] | 157.1534 |  | 0.022999
| 40098.1066 | 60.024 | 3787.5366 |  |  | 3090 | -24.7182 | -21.72 |  | 0 | 3744.2615 | 3766.1331 | 3783.0953 | 3770.5065 | 3726.8779 |  |  |  |  | 40098.1066 | 60.024 | 3787.5366 | 350 | -231.1755 | 16 |  | 10 | 0 | -103 | 7713.51 | -24.7182 | [14 empty] | 155.4742 |  | 0.023998
| 40098.1067 | 60.025 | 3785.8418 |  |  | 3090 | -25.7516 | -23.1311 |  | 0 | 3742.8504 | 3766.2385 | 3782.8801 | 3770.5065 | 3727.1124 |  |  |  |  | 40098.1067 | 60.025 | 3785.8418 | 350 | -231.1755 | 16 |  | 10 | 0 | -103 | 7713.84 | -25.7516 | [14 empty] | 153.7794 |  | 0.025002
| 40098.1067 | 60.021 | 3786.0767 |  |  | 3090 | -21.6299 | -22.6057 |  | 0 | 3743.3758 | 3766.344 | 3782.67 | 3770.5065 | 3727.3445 |  |  |  |  | 40098.1067 | 60.021 | 3786.0767 | 350 | -231.1755 | 16 |  | 10 | 0 | -103 | 7714.17 | -21.6299 | [14 empty] | 154.0142 |  | 0.021
| 40098.1067 | 60.019 | 3787.9304 |  |  | 3090 | -19.571 | -21.5435 |  | 0 | 3744.438 | 3766.4582 | 3782.4677 | 3770.5065 | 3727.5741 |  |  |  |  | 40098.1067 | 60.019 | 3787.9304 | 350 | -225.6176 | 16 |  | 10 | 0 | -103 | 7714.5 | -19.571 | [14 empty] | 155.868 |  | 0.019001
| 40098.1067 | 60.024 | 3788.7603 |  |  | 3090 | -24.7182 | -22.6547 |  | 0 | 3743.3268 | 3766.5756 | 3782.2617 | 3770.5065 | 3727.8012 |  |  |  |  | 40098.1067 | 60.024 | 3788.7603 | 350 | -225.6176 | 16 |  | 10 | 0 | -103 | 7714.83 | -24.7182 | [14 empty] | 156.6978 |  | 0.023998
| 40098.1068 | 60.024 | 3786.8748 |  |  | 3090 | -24.7182 | -23.3769 |  | 0 | 3742.6046 | 3766.6819 | 3782.0541 | 3770.5065 | 3728.026 |  |  |  |  | 40098.1068 | 60.024 | 3786.8748 | 350 | -225.6176 | 16 |  | 10 | 0 | -103 | 7715.16 | -24.7182 | [14 empty] | 154.8123 |  | 0.023998
| 40098.1068 | 60.021 | 3786.5498 |  |  | 3090 | -21.6299 | -22.7655 |  | 0 | 3743.216 | 3766.7854 | 3781.8518 | 3770.5065 | 3728.2484 |  |  |  |  | 40098.1068 | 60.021 | 3786.5498 | 350 | -225.6176 | 16 |  | 10 | 0 | -103 | 7715.49 | -21.6299 | [14 empty] | 154.4874 |  | 0.021
| 40098.1068 | 60.02 | 3787.3577 |  |  | 3090 | -20.6005 | -22.0077 |  | 0 | 3743.9738 | 3766.892 | 3781.6555 | 3770.5065 | 3728.4685 |  |  |  |  | 40098.1068 | 60.02 | 3787.3577 | 350 | -225.6176 | 16 |  | 10 | 0 | -103 | 7715.82 | -20.6005 | [14 empty] | 155.2952 |  | 0.02
| 40098.1068 | 60.025 | 3785.0181 |  |  | 3090 | -25.7516 | -23.3181 |  | 0 | 3742.6634 | 3766.9854 | 3781.4545 | 3770.5065 | 3728.6863 |  |  |  |  | 40098.1068 | 60.025 | 3785.0181 | 350 | -230.7344 | 16 |  | 10 | 0 | -103 | 7716.15 | -25.7516 | [14 empty] | 152.9556 |  | 0.025002
| 40098.1069 | 60.024 | 3785.614 |  |  | 3090 | -24.7182 | -23.8081 |  | 0 | 3742.1734 | 3767.0809 | 3781.2531 | 3770.5065 | 3728.9019 |  |  |  |  | 40098.1069 | 60.024 | 3785.614 | 350 | -230.7344 | 16 |  | 10 | 0 | -103 | 7716.48 | -24.7182 | [14 empty] | 153.5516 |  | 0.023998
| 40098.1069 | 60.02 | 3785.9492 |  |  | 3090 | -20.6005 | -22.6854 |  | 0 | 3743.2961 | 3767.1772 | 3781.0594 | 3770.5065 | 3729.1153 |  |  |  |  | 40098.1069 | 60.02 | 3785.9492 | 350 | -230.7344 | 16 |  | 10 | 0 | -103 | 7716.81 | -20.6005 | [14 empty] | 153.8868 |  | 0.02
| 40098.1069 | 60.02 | 3785.8037 |  |  | 3090 | -20.6005 | -21.9557 |  | 0 | 3744.0258 | 3767.2717 | 3780.8714 | 3770.5065 | 3729.3264 |  |  |  |  | 40098.1069 | 60.02 | 3785.8037 | 350 | -230.7344 | 16 |  | 10 | 0 | -103 | 7717.14 | -20.6005 | [14 empty] | 153.7413 |  | 0.02
| 40098.1069 | 60.022 | 3786.8643 |  |  | 3090 | -22.6593 | -22.202 |  | 0 | 3743.7795 | 3767.3707 | 3780.6841 | 3770.5065 | 3729.5355 |  |  |  |  | 40098.1069 | 60.022 | 3786.8643 | 350 | -230.7344 | 16 |  | 10 | 0 | -103 | 7717.47 | -22.6593 | [14 empty] | 154.8018 |  | 0.021999
| 40098.1069 | 60.022 | 3786.8772 |  |  | 3090 | -22.6593 | -22.3621 |  | 0 | 3743.6194 | 3767.4687 | 3780.4979 | 3770.5065 | 3729.7424 |  |  |  |  | 40098.1069 | 60.022 | 3786.8772 | 350 | -234.8471 | 16 |  | 10 | 0 | -103 | 7717.8 | -22.6593 | [14 empty] | 154.8148 |  | 0.021999
| 40098.107 | 60.022 | 3785.2539 |  |  | 3090 | -22.6593 | -22.4661 |  | 0 | 3743.5154 | 3767.5577 | 3780.3129 | 3770.5065 | 3729.9472 |  |  |  |  | 40098.107 | 60.022 | 3785.2539 | 350 | -234.8471 | 16 |  | 10 | 0 | -103 | 7718.13 | -22.6593 | [14 empty] | 153.1915 |  | 0.021999
| 40098.107 | 60.021 | 3785.7261 |  |  | 3090 | -21.6299 | -22.1734 |  | 0 | 3743.8081 | 3767.648 | 3780.1313 | 3770.5065 | 3730.15 |  |  |  |  | 40098.107 | 60.021 | 3785.7261 | 350 | -234.8471 | 16 |  | 10 | 0 | -103 | 7718.46 | -21.6299 | [14 empty] | 153.6636 |  | 0.021
| 40098.107 | 60.021 | 3786.3469 |  |  | 3090 | -21.6299 | -21.9832 |  | 0 | 3743.9983 | 3767.7406 | 3779.9525 | 3770.5065 | 3730.3508 |  |  |  |  | 40098.107 | 60.021 | 3786.3469 | 350 | -234.8471 | 16 |  | 10 | 0 | -103 | 7718.79 | -21.6299 | [14 empty] | 154.2845 |  | 0.021
| 40098.107 | 60.023 | 3785.821 |  |  | 3090 | -23.6888 | -22.5802 |  | 0 | 3743.4013 | 3767.8297 | 3779.7724 | 3770.5065 | 3730.5496 |  |  |  |  | 40098.107 | 60.023 | 3785.821 | 350 | -234.8471 | 16 |  | 10 | 0 | -103 | 7719.12 | -23.6888 | [14 empty] | 153.7586 |  | 0.022999
| 40098.1071 | 60.023 | 3785.7983 |  |  | 3090 | -23.6888 | -22.9682 |  | 0 | 3743.0133 | 3767.9178 | 3779.5922 | 3770.5065 | 3730.7464 |  |  |  |  | 40098.1071 | 60.023 | 3785.7983 | 350 | -228.9609 | 16 |  | 10 | 0 | -103 | 7719.45 | -23.6888 | [14 empty] | 153.7359 |  | 0.022999
| 40098.1071 | 60.022 | 3786.2842 |  |  | 3090 | -22.6593 | -22.8601 |  | 0 | 3743.1214 | 3768.0073 | 3779.4143 | 3770.5065 | 3730.9413 |  |  |  |  | 40098.1071 | 60.022 | 3786.2842 | 350 | -228.9609 | 16 |  | 10 | 0 | -103 | 7719.78 | -22.6593 | [14 empty] | 154.2217 |  | 0.021999
| 40098.1071 | 60.019 | 3786.9392 |  |  | 3090 | -19.571 | -21.7089 |  | 0 | 3744.2726 | 3768.0993 | 3779.2437 | 3770.5065 | 3731.1343 |  |  |  |  | 40098.1071 | 60.019 | 3786.9392 | 350 | -228.9609 | 16 |  | 10 | 0 | -103 | 7720.11 | -19.571 | [14 empty] | 154.8768 |  | 0.019001
| 40098.1071 | 60.016 | 3787.6274 |  |  | 3090 | -16.4788 | -19.8784 |  | 0 | 3746.1031 | 3768.1936 | 3779.0836 | 3770.5065 | 3731.3255 |  |  |  |  | 40098.1071 | 60.016 | 3787.6274 | 350 | -228.9609 | 16 |  | 10 | 0 | -103 | 7720.44 | -16.4788 | [14 empty] | 155.565 |  | 0.015999
| 40098.1072 | 60.018 | 3789.4443 |  |  | 3090 | -18.5416 | -19.4105 |  | 0 | 3746.571 | 3768.2958 | 3778.9273 | 3770.5065 | 3731.5147 |  |  |  |  | 40098.1072 | 60.018 | 3789.4443 | 350 | -228.9609 | 16 |  | 10 | 0 | -103 | 7720.77 | -18.5416 | [14 empty] | 157.3819 |  | 0.018002
| 40098.1072 | 60.018 | 3789.6733 |  |  | 3090 | -18.5416 | -19.1064 |  | 0 | 3746.8751 | 3768.398 | 3778.7739 | 3770.5065 | 3731.7022 |  |  |  |  | 40098.1072 | 60.018 | 3789.6733 | 350 | -231.1779 | 16 |  | 10 | 0 | -103 | 7721.1 | -18.5416 | [14 empty] | 157.6109 |  | 0.018002
| 40098.1072 | 60.018 | 3789.4043 |  |  | 3090 | -18.5416 | -18.9087 |  | 0 | 3747.0728 | 3768.4981 | 3778.623 | 3770.5065 | 3731.8879 |  |  |  |  | 40098.1072 | 60.018 | 3789.4043 | 350 | -231.1779 | 16 |  | 10 | 0 | -103 | 7721.43 | -18.5416 | [14 empty] | 157.3419 |  | 0.018002
| 40098.1072 | 60.019 | 3788.4788 |  |  | 3090 | -19.571 | -19.1405 |  | 0 | 3746.841 | 3768.5928 | 3778.4724 | 3770.5065 | 3732.0718 |  |  |  |  | 40098.1072 | 60.019 | 3788.4788 | 350 | -231.1779 | 16 |  | 10 | 0 | -103 | 7721.76 | -19.571 | [14 empty] | 156.4163 |  | 0.019001
| 40098.1072 | 60.019 | 3789.1833 |  |  | 3090 | -19.571 | -19.2912 |  | 0 | 3746.6903 | 3768.6899 | 3778.3224 | 3770.5065 | 3732.2539 |  |  |  |  | 40098.1072 | 60.019 | 3789.1833 | 350 | -231.1779 | 16 |  | 10 | 0 | -103 | 7722.09 | -19.571 | [14 empty] | 157.1209 |  | 0.019001
| 40098.1073 | 60.016 | 3789.3689 |  |  | 3090 | -16.4788 | -18.3069 |  | 0 | 3747.6746 | 3768.787 | 3778.1786 | 3770.5065 | 3732.4344 |  |  |  |  | 40098.1073 | 60.016 | 3789.3689 | 350 | -231.1779 | 16 |  | 10 | 0 | -103 | 7722.42 | -16.4788 | [14 empty] | 157.3065 |  | 0.015999
| 40098.1073 | 60.015 | 3789.0049 |  |  | 3090 | -15.4494 | -17.3067 |  | 0 | 3748.6747 | 3768.8815 | 3778.0407 | 3770.5065 | 3732.6131 |  |  |  |  | 40098.1073 | 60.015 | 3789.0049 | 350 | -236.4893 | 16 |  | 10 | 0 | -103 | 7722.75 | -15.4494 | [14 empty] | 156.9424 |  | 0.014999
| 40098.1073 | 60.016 | 3788.6646 |  |  | 3090 | -16.4788 | -17.017 |  | 0 | 3748.9645 | 3768.9735 | 3777.9054 | 3770.5065 | 3732.7902 |  |  |  |  | 40098.1073 | 60.016 | 3788.6646 | 350 | -236.4893 | 16 |  | 10 | 0 | -103 | 7723.08 | -16.4788 | [14 empty] | 156.6021 |  | 0.015999
| 40098.1073 | 60.014 | 3788.9329 |  |  | 3090 | -14.4199 | -16.108 |  | 0 | 3749.8735 | 3769.0659 | 3777.7757 | 3770.5065 | 3732.9656 |  |  |  |  | 40098.1073 | 60.014 | 3788.9329 | 350 | -236.4893 | 16 |  | 10 | 0 | -103 | 7723.41 | -14.4199 | [14 empty] | 156.8704 |  | 0.014
| 40098.1074 | 60.013 | 3790.667 |  |  | 3090 | -13.3905 | -15.1569 |  | 0 | 3750.8246 | 3769.1654 | 3777.6515 | 3770.5065 | 3733.1394 |  |  |  |  | 40098.1074 | 60.013 | 3790.667 | 350 | -236.4893 | 16 |  | 10 | 0 | -103 | 7723.74 | -13.3905 | [14 empty] | 158.6046 |  | 0.013
| 40098.1074 | 60.012 | 3790.8052 |  |  | 3090 | -12.3611 | -14.1783 |  | 0 | 3751.8031 | 3769.2647 | 3777.5329 | 3770.5065 | 3733.3116 |  |  |  |  | 40098.1074 | 60.012 | 3790.8052 | 350 | -236.4893 | 16 |  | 10 | 0 | -103 | 7724.07 | -12.3611 | [14 empty] | 158.7427 |  | 0.012001
| 40098.1074 | 60.012 | 3790.4111 |  |  | 3090 | -12.3611 | -13.5423 |  | 0 | 3752.4392 | 3769.3612 | 3777.4183 | 3770.5065 | 3733.4822 |  |  |  |  | 40098.1074 | 60.012 | 3790.4111 | 350 | -245.0389 | 16 |  | 10 | 0 | -103 | 7724.4 | -12.3611 | [14 empty] | 158.3487 |  | 0.012001
| 40098.1074 | 60.01 | 3789.7686 |  |  | 3090 | -10.2983 | -12.4069 |  | 0 | 3753.5746 | 3769.454 | 3777.3099 | 3770.5065 | 3733.6513 |  |  |  |  | 40098.1074 | 60.01 | 3789.7686 | 350 | -245.0389 | 16 |  | 10 | 0 | -103 | 7724.73 | -10.2983 | [14 empty] | 157.7061 |  | 0.0099983
| 40098.1075 | 60.007 | 3791.5398 |  |  | 3090 | -7.21 | -10.588 |  | 0 | 3755.3935 | 3769.5539 | 3777.2108 | 3770.5065 | 3733.8188 |  |  |  |  | 40098.1075 | 60.007 | 3791.5398 | 350 | -245.0389 | 16 |  | 10 | 0 | -103 | 7725.06 | -7.21 | [14 empty] | 159.4774 |  | 0.007
| 40098.1075 | 60.007 | 3792.9453 |  |  | 3090 | -7.21 | -9.4057 |  | 0 | 3756.5758 | 3769.6593 | 3777.1178 | 3770.5065 | 3733.9848 |  |  |  |  | 40098.1075 | 60.007 | 3792.9453 | 350 | -245.0389 | 16 |  | 10 | 0 | -103 | 7725.39 | -7.21 | [14 empty] | 160.8829 |  | 0.007
| 40098.1075 | 60.009 | 3791.0271 |  |  | 3090 | -9.2688 | -9.3578 |  | 0 | 3756.6237 | 3769.7551 | 3777.0259 | 3770.5065 | 3734.1493 |  |  |  |  | 40098.1075 | 60.009 | 3791.0271 | 350 | -245.0389 | 16 |  | 10 | 0 | -103 | 7725.72 | -9.2688 | [14 empty] | 158.9647 |  | 0.0089989
| 40098.1075 | 60.009 | 3791.4431 |  |  | 3090 | -9.2688 | -9.3266 |  | 0 | 3756.6548 | 3769.8519 | 3776.935 | 3770.5065 | 3734.3124 |  |  |  |  | 40098.1075 | 60.009 | 3791.4431 | 350 | -223.6057 | 16 |  | 10 | 0 | -103 | 7726.05 | -9.2688 | [14 empty] | 159.3807 |  | 0.0089989
| 40098.1075 | 60.01 | 3791.426 |  |  | 3090 | -10.2983 | -9.6667 |  | 0 | 3756.3148 | 3769.9478 | 3776.8433 | 3770.5065 | 3734.4739 |  |  |  |  | 40098.1075 | 60.01 | 3791.426 | 350 | -223.6057 | 16 |  | 10 | 0 | -103 | 7726.38 | -10.2983 | [14 empty] | 159.3636 |  | 0.0099983
| 40098.1076 | 60.003 | 3790.603 |  |  | 3090 | -3.0883 | -7.3643 |  | 0 | 3758.6172 | 3770.0392 | 3776.7627 | 3770.5065 | 3734.6341 |  |  |  |  | 40098.1076 | 60.003 | 3790.603 | 350 | -223.6057 | 16 |  | 10 | 0 | -103 | 7726.71 | -3.0883 | [14 empty] | 158.5406 |  | 0.0029984
| 40098.1076 | 59.999 | 3790.4573 |  |  | 3090 | 1.0294 | -4.4265 |  | 0 | 3761.555 | 3770.1292 | 3776.6957 | 3770.5065 | 3734.7928 |  |  |  |  | 40098.1076 | 59.999 | 3790.4573 | 350 | -223.6057 | 16 |  | 10 | 0 | -103 | 7727.04 | 1.0294 | [14 empty] | 158.3948 |  | 0.00099945
| 40098.1076 | 59.995 | 3790.2163 |  |  | 3090 | 5.1511 | -1.0743 |  | 0 | 3764.9072 | 3770.2173 | 3776.644 | 3770.5065 | 3734.9501 |  |  |  |  | 40098.1076 | 59.995 | 3790.2163 | 350 | -223.6057 | 16 |  | 10 | 0 | -103 | 7727.37 | 5.1511 | [14 empty] | 158.1539 |  | 0.0050011
| 40098.1076 | 59.992 | 3789.585 |  |  | 3090 | 8.2394 | 2.1855 |  | 0 | 3768.167 | 3770.3018 | 3776.607 | 3770.5065 | 3735.1061 |  |  |  |  | 40098.1076 | 59.992 | 3789.585 | 350 | -231.1194 | 16 |  | 10 | 0 | -103 | 7727.7 | 8.2394 | [14 empty] | 157.5225 |  | 0.0079994
| 40098.1077 | 59.991 | 3788.457 |  |  | 3090 | 9.2688 | 4.6647 |  | 0 | 3770.6461 | 3770.3808 | 3776.5811 | 3770.5065 | 3735.2607 |  |  |  |  | 40098.1077 | 59.991 | 3788.457 | 350 | -231.1194 | 16 |  | 10 | 0 | -103 | 7728.03 | 9.2688 | [14 empty] | 156.3946 |  | 0.0089989
| 40098.1077 | 59.992 | 3788.105 |  |  | 3090 | 8.2394 | 5.9158 |  | 0 | 3771.8973 | 3770.4575 | 3776.5608 | 3770.5065 | 3735.4139 |  |  |  |  | 40098.1077 | 59.992 | 3788.105 | 350 | -231.1194 | 16 |  | 10 | 0 | -103 | 7728.36 | 8.2394 | [14 empty] | 156.0425 |  | 0.0079994
| 40098.1077 | 59.992 | 3788.0571 |  |  | 3090 | 8.2394 | 6.7291 |  | 0 | 3772.7106 | 3770.5334 | 3776.5442 | 3770.5065 | 3735.5658 |  |  |  |  | 40098.1077 | 59.992 | 3788.0571 | 350 | -231.1194 | 16 |  | 10 | 0 | -103 | 7728.69 | 8.2394 | [14 empty] | 155.9947 |  | 0.0079994
| 40098.1077 | 59.988 | 3788.1895 |  |  | 3090 | 12.3611 | 8.7003 |  | 0 | 3774.6818 | 3770.6091 | 3776.5362 | 3770.5065 | 3735.7164 |  |  |  |  | 40098.1077 | 59.988 | 3788.1895 | 350 | -231.1194 | 16 |  | 10 | 0 | -103 | 7729.02 | 12.3611 | [14 empty] | 156.127 |  | 0.012001
| 40098.1078 | 59.986 | 3788.4973 |  |  | 3090 | 14.4199 | 10.7022 |  | 0 | 3776.6836 | 3770.6856 | 3776.5368 | 3770.5065 | 3735.8658 |  |  |  |  | 40098.1078 | 59.986 | 3788.4973 | 350 | -237.2066 | 16 |  | 10 | 0 | -103 | 7729.35 | 14.4199 | [14 empty] | 156.4349 |  | 0.014
| 40098.1078 | 59.985 | 3788.54 |  |  | 3090 | 15.4494 | 12.3637 |  | 0 | 3778.3452 | 3770.7616 | 3776.5445 | 3770.5065 | 3736.0138 |  |  |  |  | 40098.1078 | 59.985 | 3788.54 | 350 | -237.2066 | 16 |  | 10 | 0 | -103 | 7729.68 | 15.4494 | [14 empty] | 156.4776 |  | 0.014999
| 40098.1078 | 59.984 | 3788.5708 |  |  | 3090 | 16.4788 | 13.804 |  | 0 | 3779.7855 | 3770.837 | 3776.5582 | 3770.5065 | 3736.1606 |  |  |  |  | 40098.1078 | 59.984 | 3788.5708 | 350 | -237.2066 | 16 |  | 10 | 0 | -103 | 7730.01 | 16.4788 | [14 empty] | 156.5084 |  | 0.015999
| 40098.1078 | 59.985 | 3788.1011 |  |  | 3090 | 15.4494 | 14.3799 |  | 0 | 3780.3614 | 3770.9099 | 3776.5743 | 3770.5065 | 3736.3061 |  |  |  |  | 40098.1078 | 59.985 | 3788.1011 | 350 | -237.2066 | 16 |  | 10 | 0 | -103 | 7730.34 | 15.4494 | [14 empty] | 156.0386 |  | 0.014999
| 40098.1078 | 59.984 | 3787.1333 |  |  | 3090 | 16.4788 | 15.1145 |  | 0 | 3781.096 | 3770.978 | 3776.5933 | 3770.5065 | 3736.4504 |  |  |  |  | 40098.1078 | 59.984 | 3787.1333 | 350 | -237.2066 | 16 |  | 10 | 0 | -103 | 7730.67 | 16.4788 | [14 empty] | 155.0709 |  | 0.015999
| 40098.1079 | 59.982 | 3786.4529 |  |  | 3090 | 18.5416 | 16.314 |  | 0 | 3782.2955 | 3771.0428 | 3776.6171 | 3770.5065 | 3736.5935 |  |  |  |  | 40098.1079 | 59.982 | 3786.4529 | 350 | -240.5164 | 16 |  | 10 | 0 | -103 | 7731 | 18.5416 | [14 empty] | 154.3904 |  | 0.018002
| 40098.1079 | 59.981 | 3787.7324 |  |  | 3090 | 19.571 | 17.454 |  | 0 | 3783.4354 | 3771.1123 | 3776.6456 | 3770.5065 | 3736.7354 |  |  |  |  | 40098.1079 | 59.981 | 3787.7324 | 350 | -240.5164 | 16 |  | 10 | 0 | -103 | 7731.33 | 19.571 | [14 empty] | 155.67 |  | 0.019001
| 40098.1079 | 59.982 | 3788.8135 |  |  | 3090 | 18.5416 | 17.8346 |  | 0 | 3783.8161 | 3771.1858 | 3776.6753 | 3770.5065 | 3736.8761 |  |  |  |  | 40098.1079 | 59.982 | 3788.8135 | 350 | -240.5164 | 16 |  | 10 | 0 | -103 | 7731.66 | 18.5416 | [14 empty] | 156.751 |  | 0.018002
| 40098.1079 | 59.979 | 3789.2852 |  |  | 3090 | 21.6299 | 19.163 |  | 0 | 3785.1445 | 3771.2606 | 3776.7103 | 3770.5065 | 3737.0157 |  |  |  |  | 40098.1079 | 59.979 | 3789.2852 | 350 | -240.5164 | 16 |  | 10 | 0 | -103 | 7731.99 | 21.6299 | [14 empty] | 157.2227 |  | 0.021
| 40098.108 | 59.977 | 3788.2563 |  |  | 3090 | 23.6888 | 20.747 |  | 0 | 3786.7285 | 3771.3305 | 3776.7515 | 3770.5065 | 3737.154 |  |  |  |  | 40098.108 | 59.977 | 3788.2563 | 350 | -240.5164 | 16 |  | 10 | 0 | -103 | 7732.32 | 23.6888 | [14 empty] | 156.1939 |  | 0.022999
| 40098.108 | 59.976 | 3788.4097 |  |  | 3090 | 24.7182 | 22.1369 |  | 0 | 3788.1184 | 3771.4005 | 3776.7981 | 3770.5065 | 3737.2913 |  |  |  |  | 40098.108 | 59.976 | 3788.4097 | 350 | -237.5661 | 16 |  | 10 | 0 | -103 | 7732.65 | 24.7182 | [14 empty] | 156.3472 |  | 0.023998
| 40098.108 | 59.976 | 3790.4673 |  |  | 3090 | 24.7182 | 23.0404 |  | 0 | 3789.0219 | 3771.4783 | 3776.848 | 3770.5065 | 3737.4274 |  |  |  |  | 40098.108 | 59.976 | 3790.4673 | 350 | -237.5661 | 16 |  | 10 | 0 | -103 | 7732.98 | 24.7182 | [14 empty] | 158.4048 |  | 0.023998
| 40098.108 | 59.979 | 3790.6646 |  |  | 3090 | 21.6299 | 22.5467 |  | 0 | 3788.5282 | 3771.5563 | 3776.8955 | 3770.5065 | 3737.5624 |  |  |  |  | 40098.108 | 59.979 | 3790.6646 | 350 | -237.5661 | 16 |  | 10 | 0 | -103 | 7733.31 | 21.6299 | [14 empty] | 158.6021 |  | 0.021
| 40098.1081 | 59.982 | 3790.4204 |  |  | 3090 | 18.5416 | 21.1449 |  | 0 | 3787.1264 | 3771.6327 | 3776.9369 | 3770.5065 | 3737.6964 |  |  |  |  | 40098.1081 | 59.982 | 3790.4204 | 350 | -237.5661 | 16 |  | 10 | 0 | -103 | 7733.64 | 18.5416 | [14 empty] | 158.358 |  | 0.018002
| 40098.1081 | 59.978 | 3789.6738 |  |  | 3090 | 22.6593 | 21.675 |  | 0 | 3787.6565 | 3771.7054 | 3776.9801 | 3770.5065 | 3737.8292 |  |  |  |  | 40098.1081 | 59.978 | 3789.6738 | 350 | -237.5661 | 16 |  | 10 | 0 | -103 | 7733.97 | 22.6593 | [14 empty] | 157.6114 |  | 0.021999
| 40098.1081 | 59.976 | 3789.2671 |  |  | 3090 | 24.7182 | 22.7401 |  | 0 | 3788.7216 | 3771.776 | 3777.0273 | 3770.5065 | 3737.961 |  |  |  |  | 40098.1081 | 59.976 | 3789.2671 | 350 | -231.5814 | 16 |  | 10 | 0 | -103 | 7734.3 | 24.7182 | [14 empty] | 157.2047 |  | 0.023998
| 40098.1081 | 59.974 | 3789.1479 |  |  | 3090 | 26.781 | 24.1544 |  | 0 | 3790.1359 | 3771.8455 | 3777.0797 | 3770.5065 | 3738.0917 |  |  |  |  | 40098.1081 | 59.974 | 3789.1479 | 350 | -231.5814 | 16 |  | 10 | 0 | -103 | 7734.63 | 26.781 | [14 empty] | 157.0855 |  | 0.026001
| 40098.1081 | 59.976 | 3790.4304 |  |  | 3090 | 24.7182 | 24.3517 |  | 0 | 3790.3332 | 3771.9195 | 3777.1325 | 3770.5065 | 3738.2213 |  |  |  |  | 40098.1081 | 59.976 | 3790.4304 | 350 | -231.5814 | 16 |  | 10 | 0 | -103 | 7734.96 | 24.7182 | [14 empty] | 158.368 |  | 0.023998
| 40098.1082 | 59.977 | 3789.9143 |  |  | 3090 | 23.6888 | 24.1197 |  | 0 | 3790.1012 | 3771.9909 | 3777.184 | 3770.5065 | 3738.35 |  |  |  |  | 40098.1082 | 59.977 | 3789.9143 | 350 | -231.5814 | 16 |  | 10 | 0 | -103 | 7735.29 | 23.6888 | [14 empty] | 157.8519 |  | 0.022999
| 40098.1082 | 59.977 | 3786.2432 |  |  | 3090 | 23.6888 | 23.9689 |  | 0 | 3789.9504 | 3772.0472 | 3777.2345 | 3770.5065 | 3738.4776 |  |  |  |  | 40098.1082 | 59.977 | 3786.2432 | 350 | -231.5814 | 16 |  | 10 | 0 | -103 | 7735.62 | 23.6888 | [14 empty] | 154.1807 |  | 0.022999
| 40098.1082 | 59.975 | 3787.4421 |  |  | 3090 | 25.7516 | 24.5928 |  | 0 | 3790.5743 | 3772.1079 | 3777.287 | 3770.5065 | 3738.6042 |  |  |  |  | 40098.1082 | 59.975 | 3787.4421 | 350 | -235.8508 | 16 |  | 10 | 0 | -103 | 7735.95 | 25.7516 | [14 empty] | 155.3797 |  | 0.025002
| 40098.1082 | 59.973 | 3788.9629 |  |  | 3090 | 27.8104 | 25.719 |  | 0 | 3791.7005 | 3772.174 | 3777.3435 | 3770.5065 | 3738.7298 |  |  |  |  | 40098.1082 | 59.973 | 3788.9629 | 350 | -235.8508 | 16 |  | 10 | 0 | -103 | 7736.28 | 27.8104 | [14 empty] | 156.9005 |  | 0.027
| 40098.1083 | 59.969 | 3790.6016 |  |  | 3090 | 31.9282 | 27.8922 |  | 0 | 3793.8737 | 3772.2459 | 3777.4081 | 3770.5065 | 3738.8544 |  |  |  |  | 40098.1083 | 59.969 | 3790.6016 | 350 | -235.8508 | 16 |  | 10 | 0 | -103 | 7736.61 | 31.9282 | [14 empty] | 158.5391 |  | 0.030998
| 40098.1083 | 59.97 | 3791.877 |  |  | 3090 | 30.8987 | 28.9445 |  | 0 | 3794.926 | 3772.3223 | 3777.4762 | 3770.5065 | 3738.978 |  |  |  |  | 40098.1083 | 59.97 | 3791.877 | 350 | -235.8508 | 16 |  | 10 | 0 | -103 | 7736.94 | 30.8987 | [14 empty] | 159.8145 |  | 0.029999
| 40098.1083 | 59.971 | 3792.9106 |  |  | 3090 | 29.8693 | 29.2682 |  | 0 | 3795.2497 | 3772.4021 | 3777.5451 | 3770.5065 | 3739.1007 |  |  |  |  | 40098.1083 | 59.971 | 3792.9106 | 350 | -235.8508 | 16 |  | 10 | 0 | -103 | 7737.27 | 29.8693 | [14 empty] | 160.8482 |  | 0.028999
| 40098.1083 | 59.973 | 3792.3113 |  |  | 3090 | 27.8104 | 28.758 |  | 0 | 3794.7395 | 3772.479 | 3777.6115 | 3770.5065 | 3739.2224 |  |  |  |  | 40098.1083 | 59.973 | 3792.3113 | 350 | -233.56 | 16 |  | 10 | 0 | -103 | 7737.6 | 27.8104 | [14 empty] | 160.2488 |  | 0.027
| 40098.1084 | 59.978 | 3789.125 |  |  | 3090 | 22.6593 | 26.6234 |  | 0 | 3792.6049 | 3772.543 | 3777.6692 | 3770.5065 | 3739.3432 |  |  |  |  | 40098.1084 | 59.978 | 3789.125 | 350 | -233.56 | 16 |  | 10 | 0 | -103 | 7737.93 | 22.6593 | [14 empty] | 157.0626 |  | 0.021999
| 40098.1084 | 59.981 | 3788.0796 |  |  | 3090 | 19.571 | 24.1551 |  | 0 | 3790.1366 | 3772.6025 | 3777.7169 | 3770.5065 | 3739.4631 |  |  |  |  | 40098.1084 | 59.981 | 3788.0796 | 350 | -233.56 | 16 |  | 10 | 0 | -103 | 7738.26 | 19.571 | [14 empty] | 156.0172 |  | 0.019001
| 40098.1084 | 59.978 | 3787.844 |  |  | 3090 | 22.6593 | 23.6316 |  | 0 | 3789.6131 | 3772.6607 | 3777.7623 | 3770.5065 | 3739.582 |  |  |  |  | 40098.1084 | 59.978 | 3787.844 | 350 | -233.56 | 16 |  | 10 | 0 | -103 | 7738.59 | 22.6593 | [14 empty] | 155.7816 |  | 0.021999
| 40098.1084 | 59.975 | 3787.135 |  |  | 3090 | 25.7516 | 24.3736 |  | 0 | 3790.3551 | 3772.7158 | 3777.8102 | 3770.5065 | 3739.7 |  |  |  |  | 40098.1084 | 59.975 | 3787.135 | 350 | -233.56 | 16 |  | 10 | 0 | -103 | 7738.92 | 25.7516 | [14 empty] | 155.0726 |  | 0.025002
| 40098.1084 | 59.972 | 3787.1643 |  |  | 3090 | 28.8399 | 25.9368 |  | 0 | 3791.9183 | 3772.7705 | 3777.8637 | 3770.5065 | 3739.8172 |  |  |  |  | 40098.1084 | 59.972 | 3787.1643 | 350 | -219.01 | 16 |  | 10 | 0 | -103 | 7739.25 | 28.8399 | [14 empty] | 155.1019 |  | 0.028
| 40098.1085 | 59.976 | 3786.9961 |  |  | 3090 | 24.7182 | 25.5103 |  | 0 | 3791.4918 | 3772.8242 | 3777.9151 | 3770.5065 | 3739.9334 |  |  |  |  | 40098.1085 | 59.976 | 3786.9961 | 350 | -219.01 | 16 |  | 10 | 0 | -103 | 7739.58 | 24.7182 | [14 empty] | 154.9337 |  | 0.023998
| 40098.1085 | 59.975 | 3787.4048 |  |  | 3090 | 25.7516 | 25.5947 |  | 0 | 3791.5762 | 3772.879 | 3777.9665 | 3770.5065 | 3740.0488 |  |  |  |  | 40098.1085 | 59.975 | 3787.4048 | 350 | -219.01 | 16 |  | 10 | 0 | -103 | 7739.91 | 25.7516 | [14 empty] | 155.3423 |  | 0.025002
| 40098.1085 | 59.973 | 3786.4868 |  |  | 3090 | 27.8104 | 26.3702 |  | 0 | 3792.3517 | 3772.9299 | 3778.0203 | 3770.5065 | 3740.1633 |  |  |  |  | 40098.1085 | 59.973 | 3786.4868 | 350 | -219.01 | 16 |  | 10 | 0 | -103 | 7740.24 | 27.8104 | [14 empty] | 154.4244 |  | 0.027
| 40098.1085 | 59.969 | 3787.0791 |  |  | 3090 | 31.9282 | 28.3155 |  | 0 | 3794.297 | 3772.9827 | 3778.0811 | 3770.5065 | 3740.2769 |  |  |  |  | 40098.1085 | 59.969 | 3787.0791 | 350 | -219.01 | 16 |  | 10 | 0 | -103 | 7740.57 | 31.9282 | [14 empty] | 155.0167 |  | 0.030998
| 40098.1086 | 59.966 | 3789.2139 |  |  | 3090 | 35.0204 | 30.6622 |  | 0 | 3796.6437 | 3773.0431 | 3778.1501 | 3770.5065 | 3740.3897 |  |  |  |  | 40098.1086 | 59.966 | 3789.2139 | 350 | -205.3389 | 16 |  | 10 | 0 | -103 | 7740.9 | 35.0204 | [14 empty] | 157.1514 |  | 0.034
| 40098.1086 | 59.965 | 3790.5117 |  |  | 3090 | 36.0498 | 32.5479 |  | 0 | 3798.5294 | 3773.1078 | 3778.2255 | 3770.5065 | 3740.5017 |  |  |  |  | 40098.1086 | 59.965 | 3790.5117 | 350 | -205.3389 | 16 |  | 10 | 0 | -103 | 7741.23 | 36.0498 | [14 empty] | 158.4493 |  | 0.035
| 40098.1086 | 59.966 | 3791.2212 |  |  | 3090 | 35.0204 | 33.4133 |  | 0 | 3799.3948 | 3773.1746 | 3778.3037 | 3770.5065 | 3740.6128 |  |  |  |  | 40098.1086 | 59.966 | 3791.2212 | 350 | -205.3389 | 16 |  | 10 | 0 | -103 | 7741.56 | 35.0204 | [14 empty] | 159.1588 |  | 0.034
| 40098.1086 | 59.969 | 3792.2183 |  |  | 3090 | 31.9282 | 32.8935 |  | 0 | 3798.875 | 3773.2446 | 3778.3793 | 3770.5065 | 3740.7231 |  |  |  |  | 40098.1086 | 59.969 | 3792.2183 | 350 | -205.3389 | 16 |  | 10 | 0 | -103 | 7741.89 | 31.9282 | [14 empty] | 160.1558 |  | 0.030998
| 40098.1087 | 59.97 | 3790.9595 |  |  | 3090 | 30.8987 | 32.1953 |  | 0 | 3798.1768 | 3773.3095 | 3778.4518 | 3770.5065 | 3740.8326 |  |  |  |  | 40098.1087 | 59.97 | 3790.9595 | 350 | -205.3389 | 16 |  | 10 | 0 | -103 | 7742.22 | 30.8987 | [14 empty] | 158.897 |  | 0.029999
| 40098.1087 | 59.968 | 3788.8242 |  |  | 3090 | 32.9615 | 32.4635 |  | 0 | 3798.445 | 3773.3661 | 3778.5248 | 3770.5065 | 3740.9413 |  |  |  |  | 40098.1087 | 59.968 | 3788.8242 | 350 | -236.2854 | 16 |  | 10 | 0 | -103 | 7742.55 | 32.9615 | [14 empty] | 156.7618 |  | 0.032001
| 40098.1087 | 59.965 | 3789.0264 |  |  | 3090 | 36.0498 | 33.7187 |  | 0 | 3799.7002 | 3773.4231 | 3778.6018 | 3770.5065 | 3741.0492 |  |  |  |  | 40098.1087 | 59.965 | 3789.0264 | 350 | -236.2854 | 16 |  | 10 | 0 | -103 | 7742.88 | 36.0498 | [14 empty] | 156.9639 |  | 0.035
| 40098.1087 | 59.964 | 3789.1675 |  |  | 3090 | 37.0793 | 34.8949 |  | 0 | 3800.8764 | 3773.4801 | 3778.6825 | 3770.5065 | 3741.1563 |  |  |  |  | 40098.1087 | 59.964 | 3789.1675 | 350 | -236.2854 | 16 |  | 10 | 0 | -103 | 7743.21 | 37.0793 | [14 empty] | 157.105 |  | 0.035999
| 40098.1087 | 59.97 | 3787.394 |  |  | 3090 | 30.8987 | 33.4963 |  | 0 | 3799.4777 | 3773.5304 | 3778.7576 | 3770.5065 | 3741.2627 |  |  |  |  | 40098.1087 | 59.97 | 3787.394 | 350 | -236.2854 | 16 |  | 10 | 0 | -103 | 7743.54 | 30.8987 | [14 empty] | 155.3316 |  | 0.029999
| 40098.1088 | 59.972 | 3785.6899 |  |  | 3090 | 28.8399 | 31.8665 |  | 0 | 3797.848 | 3773.5741 | 3778.8262 | 3770.5065 | 3741.3683 |  |  |  |  | 40098.1088 | 59.972 | 3785.6899 | 350 | -236.2854 | 16 |  | 10 | 0 | -103 | 7743.87 | 28.8399 | [14 empty] | 153.6275 |  | 0.028
| 40098.1088 | 59.967 | 3784.8306 |  |  | 3090 | 33.991 | 32.6101 |  | 0 | 3798.5916 | 3773.6144 | 3778.8971 | 3770.5065 | 3741.4731 |  |  |  |  | 40098.1088 | 59.967 | 3784.8306 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7744.2 | 33.991 | [14 empty] | 152.7681 |  | 0.033001
| 40098.1088 | 59.967 | 3785.0095 |  |  | 3090 | 33.991 | 33.0934 |  | 0 | 3799.0749 | 3773.6551 | 3778.9691 | 3770.5065 | 3741.5771 |  |  |  |  | 40098.1088 | 59.967 | 3785.0095 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7744.53 | 33.991 | [14 empty] | 152.9471 |  | 0.033001
| 40098.1088 | 59.969 | 3784.3203 |  |  | 3090 | 31.9282 | 32.6856 |  | 0 | 3798.6671 | 3773.6931 | 3779.0392 | 3770.5065 | 3741.6805 |  |  |  |  | 40098.1088 | 59.969 | 3784.3203 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7744.86 | 31.9282 | [14 empty] | 152.2579 |  | 0.030998
| 40098.1089 | 59.968 | 3782.8086 |  |  | 3090 | 32.9615 | 32.7822 |  | 0 | 3798.7636 | 3773.7254 | 3779.1092 | 3770.5065 | 3741.783 |  |  |  |  | 40098.1089 | 59.968 | 3782.8086 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7745.19 | 32.9615 | [14 empty] | 150.7462 |  | 0.032001
| 40098.1089 | 59.969 | 3782.1099 |  |  | 3090 | 31.9282 | 32.4833 |  | 0 | 3798.4648 | 3773.755 | 3779.1776 | 3770.5065 | 3741.8849 |  |  |  |  | 40098.1089 | 59.969 | 3782.1099 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7745.52 | 31.9282 | [14 empty] | 150.0474 |  | 0.030998
| 40098.1089 | 59.967 | 3779.3516 |  |  | 3090 | 33.991 | 33.011 |  | 0 | 3798.9925 | 3773.7748 | 3779.2473 | 3770.5065 | 3741.986 |  |  |  |  | 40098.1089 | 59.967 | 3779.3516 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7745.85 | 33.991 | [14 empty] | 147.2891 |  | 0.033001
| 40098.1089 | 59.967 | 3779.0562 |  |  | 3090 | 33.991 | 33.354 |  | 0 | 3799.3355 | 3773.7933 | 3779.3178 | 3770.5065 | 3742.0865 |  |  |  |  | 40098.1089 | 59.967 | 3779.0562 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7746.18 | 33.991 | [14 empty] | 146.9937 |  | 0.033001
| 40098.109 | 59.966 | 3778.6333 |  |  | 3090 | 35.0204 | 33.9372 |  | 0 | 3799.9187 | 3773.8102 | 3779.3899 | 3770.5065 | 3742.1862 |  |  |  |  | 40098.109 | 59.966 | 3778.6333 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7746.51 | 35.0204 | [14 empty] | 146.5709 |  | 0.034
| 40098.109 | 59.965 | 3779.2117 |  |  | 3090 | 36.0498 | 34.6766 |  | 0 | 3800.6581 | 3773.829 | 3779.464 | 3770.5065 | 3742.2852 |  |  |  |  | 40098.109 | 59.965 | 3779.2117 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7746.84 | 36.0498 | [14 empty] | 147.1492 |  | 0.035
| 40098.109 | 59.971 | 3779.3347 |  |  | 3090 | 29.8693 | 32.9941 |  | 0 | 3798.9756 | 3773.8481 | 3779.5317 | 3770.5065 | 3742.3835 |  |  |  |  | 40098.109 | 59.971 | 3779.3347 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7747.17 | 29.8693 | [14 empty] | 147.2723 |  | 0.028999
| 40098.109 | 59.967 | 3776.4292 |  |  | 3090 | 33.991 | 33.343 |  | 0 | 3799.3245 | 3773.8571 | 3779.6002 | 3770.5065 | 3742.4812 |  |  |  |  | 40098.109 | 59.967 | 3776.4292 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7747.5 | 33.991 | [14 empty] | 144.3668 |  | 0.033001
| 40098.1091 | 59.965 | 3775.6467 |  |  | 3090 | 36.0498 | 34.2904 |  | 0 | 3800.2719 | 3773.8632 | 3779.6715 | 3770.5065 | 3742.5782 |  |  |  |  | 40098.1091 | 59.965 | 3775.6467 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7747.83 | 36.0498 | [14 empty] | 143.5843 |  | 0.035
| 40098.1091 | 59.962 | 3776.5967 |  |  | 3090 | 39.1381 | 35.9871 |  | 0 | 3801.9686 | 3773.8726 | 3779.7481 | 3770.5065 | 3742.6745 |  |  |  |  | 40098.1091 | 59.962 | 3776.5967 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7748.16 | 39.1381 | [14 empty] | 144.5342 |  | 0.037998 | -103
| 40098.1091 | 59.964 | 3776.5591 |  |  | 3090 | 37.0793 | 36.3694 |  | 0 | 3802.3509 | 3773.8818 | 3779.8255 | 3770.5065 | 3742.7701 |  |  |  |  | 40098.1091 | 59.964 | 3776.5591 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7748.49 | 37.0793 | [14 empty] | 144.4966 |  | 0.035999
| 40098.1091 | 59.97 | 3776.0229 |  |  | 3090 | 30.8987 | 34.4546 |  | 0 | 3800.4361 | 3773.8892 | 3779.8959 | 3770.5065 | 3742.8651 |  |  |  |  | 40098.1091 | 59.97 | 3776.0229 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7748.82 | 30.8987 | [14 empty] | 143.9605 |  | 0.029999
| 40098.1091 | 59.967 | 3773.1699 |  |  | 3090 | 33.991 | 34.2924 |  | 0 | 3800.2739 | 3773.8867 | 3779.9652 | 3770.5065 | 3742.9594 |  |  |  |  | 40098.1091 | 59.967 | 3773.1699 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7749.15 | 33.991 | [14 empty] | 141.1075 |  | 0.033001
| 40098.1092 | 59.969 | 3771.7305 |  |  | 3090 | 31.9282 | 33.4649 |  | 0 | 3799.4464 | 3773.8794 | 3780.0312 | 3770.5065 | 3743.0531 |  |  |  |  | 40098.1092 | 59.969 | 3771.7305 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7749.48 | 31.9282 | [14 empty] | 139.668 |  | 0.030998
| 40098.1092 | 59.968 | 3768.793 |  |  | 3090 | 32.9615 | 33.2887 |  | 0 | 3799.2702 | 3773.8622 | 3780.0962 | 3770.5065 | 3743.1462 |  |  |  |  | 40098.1092 | 59.968 | 3768.793 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7749.81 | 32.9615 | [14 empty] | 136.7305 |  | 0.032001
| 40098.1092 | 59.963 | 3768.5029 |  |  | 3090 | 38.1087 | 34.9757 |  | 0 | 3800.9572 | 3773.8442 | 3780.1664 | 3770.5065 | 3743.2386 |  |  |  |  | 40098.1092 | 59.963 | 3768.5029 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7750.14 | 38.1087 | [14 empty] | 136.4405 |  | 0.036999 | -103
| 40098.1092 | 59.965 | 3768.9175 |  |  | 3090 | 36.0498 | 35.3517 |  | 0 | 3801.3332 | 3773.8276 | 3780.2375 | 3770.5065 | 3743.3304 |  |  |  |  | 40098.1092 | 59.965 | 3768.9175 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7750.47 | 36.0498 | [14 empty] | 136.855 |  | 0.035
| 40098.1093 | 59.97 | 3767.3662 |  |  | 3090 | 30.8987 | 33.7931 |  | 0 | 3799.7746 | 3773.806 | 3780.3028 | 3770.5065 | 3743.4216 |  |  |  |  | 40098.1093 | 59.97 | 3767.3662 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7750.8 | 30.8987 | [14 empty] | 135.3038 |  | 0.029999
| 40098.1093 | 59.973 | 3764.7861 |  |  | 3090 | 27.8104 | 31.6992 |  | 0 | 3797.6807 | 3773.776 | 3780.3607 | 3770.5065 | 3743.5122 |  |  |  |  | 40098.1093 | 59.973 | 3764.7861 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7751.13 | 27.8104 | [14 empty] | 132.7237 |  | 0.027
| 40098.1093 | 59.968 | 3760.2954 |  |  | 3090 | 32.9615 | 32.141 |  | 0 | 3798.1225 | 3773.7312 | 3780.4198 | 3770.5065 | 3743.6022 |  |  |  |  | 40098.1093 | 59.968 | 3760.2954 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7751.46 | 32.9615 | [14 empty] | 128.233 |  | 0.032001
| 40098.1093 | 59.965 | 3759.5918 |  |  | 3090 | 36.0498 | 33.5091 |  | 0 | 3799.4906 | 3773.6844 | 3780.4829 | 3770.5065 | 3743.6916 |  |  |  |  | 40098.1093 | 59.965 | 3759.5918 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7751.79 | 36.0498 | [14 empty] | 127.5294 |  | 0.035
| 40098.1094 | 59.968 | 3761.8938 |  |  | 3090 | 32.9615 | 33.3175 |  | 0 | 3799.2989 | 3773.6454 | 3780.545 | 3770.5065 | 3743.7804 |  |  |  |  | 40098.1094 | 59.968 | 3761.8938 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7752.12 | 32.9615 | [14 empty] | 129.8314 |  | 0.032001
| 40098.1094 | 59.969 | 3761.7766 |  |  | 3090 | 31.9282 | 32.8312 |  | 0 | 3798.8127 | 3773.6064 | 3780.6051 | 3770.5065 | 3743.8686 |  |  |  |  | 40098.1094 | 59.969 | 3761.7766 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7752.45 | 31.9282 | [14 empty] | 129.7142 |  | 0.030998
| 40098.1094 | 59.967 | 3760.5825 |  |  | 3090 | 33.991 | 33.2371 |  | 0 | 3799.2186 | 3773.5637 | 3780.6661 | 3770.5065 | 3743.9562 |  |  |  |  | 40098.1094 | 59.967 | 3760.5825 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7752.78 | 33.991 | [14 empty] | 128.5201 |  | 0.033001
| 40098.1094 | 59.964 | 3760.1575 |  |  | 3090 | 37.0793 | 34.5819 |  | 0 | 3800.5634 | 3773.5199 | 3780.7311 | 3770.5065 | 3744.0432 |  |  |  |  | 40098.1094 | 59.964 | 3760.1575 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7753.11 | 37.0793 | [14 empty] | 128.095 |  | 0.035999
| 40098.1094 | 59.966 | 3759.781 |  |  | 3090 | 35.0204 | 34.7354 |  | 0 | 3800.7169 | 3773.4751 | 3780.7962 | 3770.5065 | 3744.1297 |  |  |  |  | 40098.1094 | 59.966 | 3759.781 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7753.44 | 35.0204 | [14 empty] | 127.7186 |  | 0.034
| 40098.1095 | 59.979 | 3759.4949 |  |  | 3090 | 21.6299 | 30.1485 |  | 0 | 3796.1299 | 3773.4297 | 3780.846 | 3770.5065 | 3744.2156 |  |  |  |  | 40098.1095 | 59.979 | 3759.4949 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7753.77 | 21.6299 | [14 empty] | 127.4324 |  | 0.021
| 40098.1095 | 59.99 | 3757.7729 |  |  | 3090 | 10.2983 | 23.2009 |  | 0 | 3789.1824 | 3773.3791 | 3780.873 | 3770.5065 | 3744.301 |  |  |  |  | 40098.1095 | 59.99 | 3757.7729 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7754.1 | 10.2983 | [14 empty] | 125.7105 |  | 0.0099983
| 40098.1095 | 59.983 | 3753.2771 |  |  | 3090 | 17.5082 | 21.2085 |  | 0 | 3787.19 | 3773.3142 | 3780.8934 | 3770.5065 | 3744.3858 |  |  |  |  | 40098.1095 | 59.983 | 3753.2771 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7754.43 | 17.5082 | [14 empty] | 121.2147 |  | 0.016998
| 40098.1095 | 59.974 | 3753.0874 |  |  | 3090 | 26.781 | 23.1589 |  | 0 | 3789.1403 | 3773.2492 | 3780.9199 | 3770.5065 | 3744.4701 |  |  |  |  | 40098.1095 | 59.974 | 3753.0874 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7754.76 | 26.781 | [14 empty] | 121.025 |  | 0.026001
| 40098.1096 | 59.967 | 3751.6367 |  |  | 3090 | 33.991 | 26.9501 |  | 0 | 3792.9316 | 3773.1799 | 3780.9584 | 3770.5065 | 3744.5538 |  |  |  |  | 40098.1096 | 59.967 | 3751.6367 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7755.09 | 33.991 | [14 empty] | 119.5743 |  | 0.033001
| 40098.1096 | 59.965 | 3753.751 |  |  | 3090 | 36.0498 | 30.135 |  | 0 | 3796.1165 | 3773.1178 | 3781.0068 | 3770.5065 | 3744.637 |  |  |  |  | 40098.1096 | 59.965 | 3753.751 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7755.42 | 36.0498 | [14 empty] | 121.6885 |  | 0.035
| 40098.1096 | 59.962 | 3758.2246 |  |  | 3090 | 39.1381 | 33.2861 |  | 0 | 3799.2676 | 3773.0704 | 3781.065 | 3770.5065 | 3744.7196 |  |  |  |  | 40098.1096 | 59.962 | 3758.2246 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7755.75 | 39.1381 | [14 empty] | 126.1622 |  | 0.037998 | -103
| 40098.1096 | 59.962 | 3759.2498 |  |  | 3090 | 39.1381 | 35.3343 |  | 0 | 3801.3158 | 3773.0265 | 3781.1293 | 3770.5065 | 3744.8017 |  |  |  |  | 40098.1096 | 59.962 | 3759.2498 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7756.08 | 39.1381 | [14 empty] | 127.1873 |  | 0.037998 | -103
| 40098.1097 | 59.961 | 3758.041 |  |  | 3090 | 40.1715 | 37.0273 |  | 0 | 3803.0088 | 3772.9791 | 3781.1985 | 3770.5065 | 3744.8834 |  |  |  |  | 40098.1097 | 59.961 | 3758.041 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7756.41 | 40.1715 | [14 empty] | 125.9786 |  | 0.039001 | -103
| 40098.1097 | 59.961 | 3760.9648 |  |  | 3090 | 40.1715 | 38.1278 |  | 0 | 3804.1093 | 3772.9412 | 3781.2708 | 3770.5065 | 3744.9644 |  |  |  |  | 40098.1097 | 59.961 | 3760.9648 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7756.74 | 40.1715 | [14 empty] | 128.9024 |  | 0.039001 | -103
| 40098.1097 | 59.96 | 3762.0222 |  |  | 3090 | 41.2009 | 39.2034 |  | 0 | 3805.1849 | 3772.9069 | 3781.346 | 3770.5065 | 3745.045 |  |  |  |  | 40098.1097 | 59.96 | 3762.0222 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7757.07 | 41.2009 | [14 empty] | 129.9598 |  | 0.040001 | -103
| 40098.1097 | 59.963 | 3763.8223 |  |  | 3090 | 38.1087 | 38.8203 |  | 0 | 3804.8017 | 3772.8784 | 3781.4195 | 3770.5065 | 3745.1251 |  |  |  |  | 40098.1097 | 59.963 | 3763.8223 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7757.4 | 38.1087 | [14 empty] | 131.7598 |  | 0.036999 | -103
| 40098.1097 | 59.959 | 3763.1001 |  |  | 3090 | 42.2304 | 40.0138 |  | 0 | 3805.9953 | 3772.8478 | 3781.4963 | 3770.5065 | 3745.2046 |  |  |  |  | 40098.1097 | 59.959 | 3763.1001 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7757.73 | 42.2304 | [14 empty] | 131.0377 |  | 0.041 | -103
| 40098.1098 | 59.956 | 3763.8582 |  |  | 3090 | 45.3187 | 41.8705 |  | 0 | 3807.852 | 3772.8198 | 3781.5784 | 3770.5065 | 3745.2837 |  |  |  |  | 40098.1098 | 59.956 | 3763.8582 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7758.06 | 45.3187 | [14 empty] | 131.7957 |  | 0.043999 | -103
| 40098.1098 | 59.951 | 3764.1577 |  |  | 3090 | 50.4698 | 44.8803 |  | 0 | 3810.8617 | 3772.7929 | 3781.6694 | 3770.5065 | 3745.3623 |  |  |  |  | 40098.1098 | 59.951 | 3764.1577 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7758.39 | 50.4698 | [14 empty] | 132.0953 |  | 0.049 | -103
| 40098.1098 | 59.953 | 3766.1267 |  |  | 3090 | 48.4109 | 46.116 |  | 0 | 3812.0975 | 3772.7723 | 3781.7636 | 3770.5065 | 3745.4404 |  |  |  |  | 40098.1098 | 59.953 | 3766.1267 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7758.72 | 48.4109 | [14 empty] | 134.0643 |  | 0.047001 | -103
| 40098.1098 | 59.954 | 3768.3389 |  |  | 3090 | 47.3815 | 46.5589 |  | 0 | 3812.5404 | 3772.7586 | 3781.8586 | 3770.5065 | 3745.518 |  |  |  |  | 40098.1098 | 59.954 | 3768.3389 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7759.05 | 47.3815 | [14 empty] | 136.2764 |  | 0.046001 | -103
| 40098.1099 | 59.957 | 3767.9722 |  |  | 3090 | 44.2892 | 45.7645 |  | 0 | 3811.746 | 3772.7439 | 3781.9505 | 3770.5065 | 3745.5951 |  |  |  |  | 40098.1099 | 59.957 | 3767.9722 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7759.38 | 44.2892 | [14 empty] | 135.9097 |  | 0.042999 | -103
| 40098.1099 | 59.956 | 3767.4375 |  |  | 3090 | 45.3187 | 45.6085 |  | 0 | 3811.59 | 3772.7276 | 3782.0414 | 3770.5065 | 3745.6718 |  |  |  |  | 40098.1099 | 59.956 | 3767.4375 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7759.71 | 45.3187 | [14 empty] | 135.3751 |  | 0.043999 | -103
| 40098.1099 | 59.961 | 3765.6064 |  |  | 3090 | 40.1715 | 43.7055 |  | 0 | 3809.687 | 3772.7058 | 3782.126 | 3770.5065 | 3745.7479 |  |  |  |  | 40098.1099 | 59.961 | 3765.6064 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7760.04 | 40.1715 | [14 empty] | 133.544 |  | 0.039001 | -103
| 40098.1099 | 59.963 | 3762.688 |  |  | 3090 | 38.1087 | 41.7466 |  | 0 | 3807.7281 | 3772.6753 | 3782.204 | 3770.5065 | 3745.8237 |  |  |  |  | 40098.1099 | 59.963 | 3762.688 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7760.37 | 38.1087 | [14 empty] | 130.6255 |  | 0.036999 | -103
| 40098.11 | 59.961 | 3761.5703 |  |  | 3090 | 40.1715 | 41.1954 |  | 0 | 3807.1768 | 3772.6415 | 3782.2799 | 3770.5065 | 3745.8989 |  |  |  |  | 40098.11 | 59.961 | 3761.5703 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7760.7 | 40.1715 | [14 empty] | 129.5079 |  | 0.039001 | -103
| 40098.11 | 59.959 | 3761.9199 |  |  | 3090 | 42.2304 | 41.5576 |  | 0 | 3807.5391 | 3772.609 | 3782.3565 | 3770.5065 | 3745.9737 |  |  |  |  | 40098.11 | 59.959 | 3761.9199 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7761.03 | 42.2304 | [14 empty] | 129.8575 |  | 0.041 | -103
| 40098.11 | 59.963 | 3759.627 |  |  | 3090 | 38.1087 | 40.3505 |  | 0 | 3806.332 | 3772.5698 | 3782.4289 | 3770.5065 | 3746.048 |  |  |  |  | 40098.11 | 59.963 | 3759.627 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7761.36 | 38.1087 | [14 empty] | 127.5645 |  | 0.036999 | -103
| 40098.11 | 59.963 | 3758.522 |  |  | 3090 | 38.1087 | 39.5659 |  | 0 | 3805.5474 | 3772.5275 | 3782.4985 | 3770.5065 | 3746.1219 |  |  |  |  | 40098.11 | 59.963 | 3758.522 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7761.69 | 38.1087 | [14 empty] | 126.4595 |  | 0.036999 | -103
| 40098.11 | 59.965 | 3752.4287 |  |  | 3090 | 36.0498 | 38.3353 |  | 0 | 3804.3168 | 3772.4672 | 3782.5641 | 3770.5065 | 3746.1954 |  |  |  |  | 40098.11 | 59.965 | 3752.4287 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7762.02 | 36.0498 | [14 empty] | 120.3663 |  | 0.035
| 40098.1101 | 59.968 | 3750.1016 |  |  | 3090 | 32.9615 | 36.4545 |  | 0 | 3802.4359 | 3772.4002 | 3782.6236 | 3770.5065 | 3746.2684 |  |  |  |  | 40098.1101 | 59.968 | 3750.1016 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7762.35 | 32.9615 | [14 empty] | 118.0391 |  | 0.032001
| 40098.1101 | 59.968 | 3753.8296 |  |  | 3090 | 32.9615 | 35.2319 |  | 0 | 3801.2134 | 3772.3448 | 3782.6791 | 3770.5065 | 3746.341 |  |  |  |  | 40098.1101 | 59.968 | 3753.8296 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7762.68 | 32.9615 | [14 empty] | 121.7672 |  | 0.032001
| 40098.1101 | 59.968 | 3753.5103 |  |  | 3090 | 32.9615 | 34.4373 |  | 0 | 3800.4188 | 3772.2887 | 3782.7319 | 3770.5065 | 3746.4131 |  |  |  |  | 40098.1101 | 59.968 | 3753.5103 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7763.01 | 32.9615 | [14 empty] | 121.4478 |  | 0.032001
| 40098.1101 | 59.97 | 3753.5229 |  |  | 3090 | 30.8987 | 33.1988 |  | 0 | 3799.1803 | 3772.233 | 3782.7807 | 3770.5065 | 3746.4848 |  |  |  |  | 40098.1101 | 59.97 | 3753.5229 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7763.34 | 30.8987 | [14 empty] | 121.4605 |  | 0.029999
| 40098.1102 | 59.973 | 3752.7407 |  |  | 3090 | 27.8104 | 31.3129 |  | 0 | 3797.2944 | 3772.1754 | 3782.8236 | 3770.5065 | 3746.5561 |  |  |  |  | 40098.1102 | 59.973 | 3752.7407 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7763.67 | 27.8104 | [14 empty] | 120.6783 |  | 0.027
| 40098.1102 | 59.971 | 3753.1782 |  |  | 3090 | 29.8693 | 30.8076 |  | 0 | 3796.7891 | 3772.1193 | 3782.8648 | 3770.5065 | 3746.6269 |  |  |  |  | 40098.1102 | 59.971 | 3753.1782 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7764 | 29.8693 | [14 empty] | 121.1158 |  | 0.028999
| 40098.1102 | 59.965 | 3752.729 |  |  | 3090 | 36.0498 | 32.6424 |  | 0 | 3798.6239 | 3772.0623 | 3782.9111 | 3770.5065 | 3746.6974 |  |  |  |  | 40098.1102 | 59.965 | 3752.729 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7764.33 | 36.0498 | [14 empty] | 120.6666 |  | 0.035
| 40098.1102 | 59.967 | 3753.2905 |  |  | 3090 | 33.991 | 33.1144 |  | 0 | 3799.0959 | 3772.0072 | 3782.9586 | 3770.5065 | 3746.7674 |  |  |  |  | 40098.1102 | 59.967 | 3753.2905 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7764.66 | 33.991 | [14 empty] | 121.2281 |  | 0.033001
| 40098.1103 | 59.967 | 3752.8716 |  |  | 3090 | 33.991 | 33.4212 |  | 0 | 3799.4027 | 3771.9513 | 3783.0067 | 3770.5065 | 3746.837 |  |  |  |  | 40098.1103 | 59.967 | 3752.8716 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7764.99 | 33.991 | [14 empty] | 120.8091 |  | 0.033001
| 40098.1103 | 59.972 | 3752.3586 |  |  | 3090 | 28.8399 | 31.8177 |  | 0 | 3797.7992 | 3771.8942 | 3783.0498 | 3770.5065 | 3746.9062 |  |  |  |  | 40098.1103 | 59.972 | 3752.3586 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7765.32 | 28.8399 | [14 empty] | 120.2962 |  | 0.028
| 40098.1103 | 59.976 | 3749.3979 |  |  | 3090 | 24.7182 | 29.3329 |  | 0 | 3795.3144 | 3771.8288 | 3783.0855 | 3770.5065 | 3746.975 |  |  |  |  | 40098.1103 | 59.976 | 3749.3979 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7765.65 | 24.7182 | [14 empty] | 117.3355 |  | 0.023998
| 40098.1103 | 59.975 | 3747.4758 |  |  | 3090 | 25.7516 | 28.0794 |  | 0 | 3794.0609 | 3771.7582 | 3783.1173 | 3770.5065 | 3747.0434 |  |  |  |  | 40098.1103 | 59.975 | 3747.4758 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7765.98 | 25.7516 | [14 empty] | 115.4134 |  | 0.025002
| 40098.1103 | 59.969 | 3740.3704 |  |  | 3090 | 31.9282 | 29.4265 |  | 0 | 3795.408 | 3771.6675 | 3783.1528 | 3770.5065 | 3747.1115 |  |  |  |  | 40098.1103 | 59.969 | 3740.3704 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7766.31 | 31.9282 | [14 empty] | 108.3079 |  | 0.030998
| 40098.1104 | 59.973 | 3741.2852 |  |  | 3090 | 27.8104 | 28.8609 |  | 0 | 3794.8424 | 3771.5799 | 3783.1865 | 3770.5065 | 3747.1791 |  |  |  |  | 40098.1104 | 59.973 | 3741.2852 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7766.64 | 27.8104 | [14 empty] | 109.2227 |  | 0.027
| 40098.1104 | 59.974 | 3746.6509 |  |  | 3090 | 26.781 | 28.1329 |  | 0 | 3794.1144 | 3771.5083 | 3783.2179 | 3770.5065 | 3747.2463 |  |  |  |  | 40098.1104 | 59.974 | 3746.6509 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7766.97 | 26.781 | [14 empty] | 114.5884 |  | 0.026001
| 40098.1104 | 59.978 | 3745.7383 |  |  | 3090 | 22.6593 | 26.2172 |  | 0 | 3792.1987 | 3771.4344 | 3783.2436 | 3770.5065 | 3747.3131 |  |  |  |  | 40098.1104 | 59.978 | 3745.7383 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7767.3 | 22.6593 | [14 empty] | 113.6758 |  | 0.021999
| 40098.1104 | 59.981 | 3743.3506 |  |  | 3090 | 19.571 | 23.891 |  | 0 | 3789.8725 | 3771.3542 | 3783.2626 | 3770.5065 | 3747.3796 |  |  |  |  | 40098.1104 | 59.981 | 3743.3506 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7767.63 | 19.571 | [14 empty] | 111.2881 |  | 0.019001
| 40098.1105 | 59.981 | 3741.6182 |  |  | 3090 | 19.571 | 22.379 |  | 0 | 3788.3605 | 3771.2695 | 3783.2771 | 3770.5065 | 3747.4457 |  |  |  |  | 40098.1105 | 59.981 | 3741.6182 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7767.96 | 19.571 | [14 empty] | 109.5557 |  | 0.019001
| 40098.1105 | 59.981 | 3740.3064 |  |  | 3090 | 19.571 | 21.3962 |  | 0 | 3787.3777 | 3771.1815 | 3783.2887 | 3770.5065 | 3747.5114 |  |  |  |  | 40098.1105 | 59.981 | 3740.3064 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7768.29 | 19.571 | [14 empty] | 108.244 |  | 0.019001
| 40098.1105 | 59.982 | 3738.4844 |  |  | 3090 | 18.5416 | 20.3971 |  | 0 | 3786.3786 | 3771.0889 | 3783.2975 | 3770.5065 | 3747.5767 |  |  |  |  | 40098.1105 | 59.982 | 3738.4844 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7768.62 | 18.5416 | [14 empty] | 106.4219 |  | 0.018002
| 40098.1105 | 59.982 | 3738.9014 |  |  | 3090 | 18.5416 | 19.7477 |  | 0 | 3785.7292 | 3770.998 | 3783.3044 | 3770.5065 | 3747.6417 |  |  |  |  | 40098.1105 | 59.982 | 3738.9014 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7768.95 | 18.5416 | [14 empty] | 106.8389 |  | 0.018002
| 40098.1106 | 59.984 | 3737.4036 |  |  | 3090 | 16.4788 | 18.6036 |  | 0 | 3784.5851 | 3770.9033 | 3783.308 | 3770.5065 | 3747.7062 |  |  |  |  | 40098.1106 | 59.984 | 3737.4036 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7769.28 | 16.4788 | [14 empty] | 105.3411 |  | 0.015999
| 40098.1106 | 59.982 | 3737.2732 |  |  | 3090 | 18.5416 | 18.5819 |  | 0 | 3784.5634 | 3770.8089 | 3783.3115 | 3770.5065 | 3747.7705 |  |  |  |  | 40098.1106 | 59.982 | 3737.2732 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7769.61 | 18.5416 | [14 empty] | 105.2108 |  | 0.018002
| 40098.1106 | 59.981 | 3736.3083 |  |  | 3090 | 19.571 | 18.9281 |  | 0 | 3784.9096 | 3770.7122 | 3783.316 | 3770.5065 | 3747.8343 |  |  |  |  | 40098.1106 | 59.981 | 3736.3083 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7769.94 | 19.571 | [14 empty] | 104.2459 |  | 0.019001
| 40098.1106 | 59.979 | 3736.272 |  |  | 3090 | 21.6299 | 19.8737 |  | 0 | 3785.8552 | 3770.616 | 3783.3231 | 3770.5065 | 3747.8978 |  |  |  |  | 40098.1106 | 59.979 | 3736.272 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7770.27 | 21.6299 | [14 empty] | 104.2095 |  | 0.021
| 40098.1106 | 59.98 | 3735.4482 |  |  | 3090 | 20.6005 | 20.1281 |  | 0 | 3786.1096 | 3770.5181 | 3783.3308 | 3770.5065 | 3747.961 |  |  |  |  | 40098.1106 | 59.98 | 3735.4482 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7770.6 | 20.6005 | [14 empty] | 103.3858 |  | 0.02
| 40098.1107 | 59.978 | 3735.6497 |  |  | 3090 | 22.6593 | 21.014 |  | 0 | 3786.9955 | 3770.4212 | 3783.341 | 3770.5065 | 3748.0238 |  |  |  |  | 40098.1107 | 59.978 | 3735.6497 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7770.93 | 22.6593 | [14 empty] | 103.5872 |  | 0.021999
| 40098.1107 | 59.978 | 3737.5405 |  |  | 3090 | 22.6593 | 21.5899 |  | 0 | 3787.5714 | 3770.3301 | 3783.3527 | 3770.5065 | 3748.0862 |  |  |  |  | 40098.1107 | 59.978 | 3737.5405 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7771.26 | 22.6593 | [14 empty] | 105.4781 |  | 0.021999
| 40098.1107 | 59.98 | 3738.012 |  |  | 3090 | 20.6005 | 21.2436 |  | 0 | 3787.2251 | 3770.2408 | 3783.3634 | 3770.5065 | 3748.1484 |  |  |  |  | 40098.1107 | 59.98 | 3738.012 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7771.59 | 20.6005 | [14 empty] | 105.9495 |  | 0.02
| 40098.1107 | 59.981 | 3736.7476 |  |  | 3090 | 19.571 | 20.6582 |  | 0 | 3786.6397 | 3770.1486 | 3783.3725 | 3770.5065 | 3748.2101 |  |  |  |  | 40098.1107 | 59.981 | 3736.7476 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7771.92 | 19.571 | [14 empty] | 104.6851 |  | 0.019001
| 40098.1108 | 59.98 | 3736.6931 |  |  | 3090 | 20.6005 | 20.638 |  | 0 | 3786.6195 | 3770.0567 | 3783.3814 | 3770.5065 | 3748.2715 |  |  |  |  | 40098.1108 | 59.98 | 3736.6931 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7772.25 | 20.6005 | [14 empty] | 104.6307 |  | 0.02
| 40098.1108 | 59.978 | 3736.0674 |  |  | 3090 | 22.6593 | 21.3455 |  | 0 | 3787.327 | 3769.9635 | 3783.3922 | 3770.5065 | 3748.3326 |  |  |  |  | 40098.1108 | 59.978 | 3736.0674 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7772.58 | 22.6593 | [14 empty] | 104.0049 |  | 0.021999
| 40098.1108 | 59.976 | 3736.0942 |  |  | 3090 | 24.7182 | 22.5259 |  | 0 | 3788.5074 | 3769.871 | 3783.4062 | 3770.5065 | 3748.3934 |  |  |  |  | 40098.1108 | 59.976 | 3736.0942 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7772.91 | 24.7182 | [14 empty] | 104.0318 |  | 0.023998
| 40098.1108 | 59.972 | 3736.575 |  |  | 3090 | 28.8399 | 24.7358 |  | 0 | 3790.7173 | 3769.7803 | 3783.4261 | 3770.5065 | 3748.4538 |  |  |  |  | 40098.1108 | 59.972 | 3736.575 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7773.24 | 28.8399 | [14 empty] | 104.5125 |  | 0.028
| 40098.1109 | 59.971 | 3738.571 |  |  | 3090 | 29.8693 | 26.5325 |  | 0 | 3792.514 | 3769.6955 | 3783.4508 | 3770.5065 | 3748.5139 |  |  |  |  | 40098.1109 | 59.971 | 3738.571 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7773.57 | 29.8693 | [14 empty] | 106.5086 |  | 0.028999
| 40098.1109 | 59.969 | 3738.8748 |  |  | 3090 | 31.9282 | 28.421 |  | 0 | 3794.4025 | 3769.6119 | 3783.4805 | 3770.5065 | 3748.5736 |  |  |  |  | 40098.1109 | 59.969 | 3738.8748 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7773.9 | 31.9282 | [14 empty] | 106.8123 |  | 0.030998
| 40098.1109 | 59.974 | 3738.9346 |  |  | 3090 | 26.781 | 27.847 |  | 0 | 3793.8285 | 3769.529 | 3783.5084 | 3770.5065 | 3748.6331 |  |  |  |  | 40098.1109 | 59.974 | 3738.9346 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7774.23 | 26.781 | [14 empty] | 106.8721 |  | 0.026001
| 40098.1109 | 59.975 | 3738.647 |  |  | 3090 | 25.7516 | 27.1136 |  | 0 | 3793.0951 | 3769.4458 | 3783.5343 | 3770.5065 | 3748.6922 |  |  |  |  | 40098.1109 | 59.975 | 3738.647 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7774.56 | 25.7516 | [14 empty] | 106.5845 |  | 0.025002
| 40098.1109 | 59.976 | 3737.6841 |  |  | 3090 | 24.7182 | 26.2752 |  | 0 | 3792.2567 | 3769.3604 | 3783.5577 | 3770.5065 | 3748.751 |  |  |  |  | 40098.1109 | 59.976 | 3737.6841 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7774.89 | 24.7182 | [14 empty] | 105.6216 |  | 0.023998
| 40098.111 | 59.972 | 3737.3821 |  |  | 3090 | 28.8399 | 27.1728 |  | 0 | 3793.1543 | 3769.2747 | 3783.5834 | 3770.5065 | 3748.8095 |  |  |  |  | 40098.111 | 59.972 | 3737.3821 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7775.22 | 28.8399 | [14 empty] | 105.3196 |  | 0.028
| 40098.111 | 59.969 | 3737.8921 |  |  | 3090 | 31.9282 | 28.8372 |  | 0 | 3794.8187 | 3769.1908 | 3783.6135 | 3770.5065 | 3748.8676 |  |  |  |  | 40098.111 | 59.969 | 3737.8921 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7775.55 | 31.9282 | [14 empty] | 105.8297 |  | 0.030998
| 40098.111 | 59.971 | 3740.0168 |  |  | 3090 | 29.8693 | 29.1984 |  | 0 | 3795.1799 | 3769.113 | 3783.6443 | 3770.5065 | 3748.9255 |  |  |  |  | 40098.111 | 59.971 | 3740.0168 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7775.88 | 29.8693 | [14 empty] | 107.9544 |  | 0.028999
| 40098.111 | 59.974 | 3740.3289 |  |  | 3090 | 26.781 | 28.3523 |  | 0 | 3794.3338 | 3769.0364 | 3783.6728 | 3770.5065 | 3748.9831 |  |  |  |  | 40098.111 | 59.974 | 3740.3289 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7776.21 | 26.781 | [14 empty] | 108.2664 |  | 0.026001
| 40098.1111 | 59.972 | 3742.0527 |  |  | 3090 | 28.8399 | 28.523 |  | 0 | 3794.5045 | 3768.9648 | 3783.7015 | 3770.5065 | 3749.0403 |  |  |  |  | 40098.1111 | 59.972 | 3742.0527 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7776.54 | 28.8399 | [14 empty] | 109.9903 |  | 0.028
| 40098.1111 | 59.972 | 3742.4238 |  |  | 3090 | 28.8399 | 28.6339 |  | 0 | 3794.6154 | 3768.8946 | 3783.7304 | 3770.5065 | 3749.0972 |  |  |  |  | 40098.1111 | 59.972 | 3742.4238 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7776.87 | 28.8399 | [14 empty] | 110.3614 |  | 0.028
| 40098.1111 | 59.972 | 3742.5244 |  |  | 3090 | 28.8399 | 28.706 |  | 0 | 3794.6875 | 3768.825 | 3783.7593 | 3770.5065 | 3749.1539 |  |  |  |  | 40098.1111 | 59.972 | 3742.5244 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7777.2 | 28.8399 | [14 empty] | 110.462 |  | 0.028
| 40098.1111 | 59.977 | 3742.2451 |  |  | 3090 | 23.6888 | 26.95 |  | 0 | 3792.9315 | 3768.7551 | 3783.7834 | 3770.5065 | 3749.2102 |  |  |  |  | 40098.1111 | 59.977 | 3742.2451 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7777.53 | 23.6888 | [14 empty] | 110.1827 |  | 0.022999
| 40098.1112 | 59.982 | 3741.7231 |  |  | 3090 | 18.5416 | 24.007 |  | 0 | 3789.9885 | 3768.6842 | 3783.7997 | 3770.5065 | 3749.2663 |  |  |  |  | 40098.1112 | 59.982 | 3741.7231 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7777.86 | 18.5416 | [14 empty] | 109.6607 |  | 0.018002
| 40098.1112 | 59.978 | 3740.0854 |  |  | 3090 | 22.6593 | 23.5353 |  | 0 | 3789.5168 | 3768.6093 | 3783.8147 | 3770.5065 | 3749.322 |  |  |  |  | 40098.1112 | 59.978 | 3740.0854 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7778.19 | 22.6593 | [14 empty] | 108.023 |  | 0.021999
| 40098.1112 | 59.976 | 3740.6292 |  |  | 3090 | 24.7182 | 23.9493 |  | 0 | 3789.9308 | 3768.5362 | 3783.8306 | 3770.5065 | 3749.3775 |  |  |  |  | 40098.1112 | 59.976 | 3740.6292 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7778.52 | 24.7182 | [14 empty] | 108.5667 |  | 0.023998
| 40098.1112 | 59.973 | 3739.9644 |  |  | 3090 | 27.8104 | 25.3007 |  | 0 | 3791.2822 | 3768.4618 | 3783.85 | 3770.5065 | 3749.4326 |  |  |  |  | 40098.1112 | 59.973 | 3739.9644 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7778.85 | 27.8104 | [14 empty] | 107.9019 |  | 0.027
| 40098.1112 | 59.974 | 3740.7751 |  |  | 3090 | 26.781 | 25.8188 |  | 0 | 3791.8003 | 3768.3899 | 3783.8707 | 3770.5065 | 3749.4875 |  |  |  |  | 40098.1112 | 59.974 | 3740.7751 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7779.18 | 26.781 | [14 empty] | 108.7127 |  | 0.026001
| 40098.1113 | 59.977 | 3742.8325 |  |  | 3090 | 23.6888 | 25.0733 |  | 0 | 3791.0548 | 3768.3237 | 3783.8893 | 3770.5065 | 3749.5421 |  |  |  |  | 40098.1113 | 59.977 | 3742.8325 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7779.51 | 23.6888 | [14 empty] | 110.7701 |  | 0.022999
| 40098.1113 | 59.977 | 3741.2678 |  |  | 3090 | 23.6888 | 24.5887 |  | 0 | 3790.5702 | 3768.2538 | 3783.9066 | 3770.5065 | 3749.5964 |  |  |  |  | 40098.1113 | 59.977 | 3741.2678 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7779.84 | 23.6888 | [14 empty] | 109.2054 |  | 0.022999
| 40098.1113 | 59.978 | 3739.7761 |  |  | 3090 | 22.6593 | 23.9134 |  | 0 | 3789.8949 | 3768.1804 | 3783.922 | 3770.5065 | 3749.6505 |  |  |  |  | 40098.1113 | 59.978 | 3739.7761 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7780.17 | 22.6593 | [14 empty] | 107.7137 |  | 0.021999
| 40098.1113 | 59.979 | 3738.9658 |  |  | 3090 | 21.6299 | 23.1142 |  | 0 | 3789.0957 | 3768.1053 | 3783.9353 | 3770.5065 | 3749.7042 |  |  |  |  | 40098.1113 | 59.979 | 3738.9658 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7780.5 | 21.6299 | [14 empty] | 106.9034 |  | 0.021
| 40098.1114 | 59.981 | 3738.7061 |  |  | 3090 | 19.571 | 21.8741 |  | 0 | 3787.8556 | 3768.0299 | 3783.9453 | 3770.5065 | 3749.7577 |  |  |  |  | 40098.1114 | 59.981 | 3738.7061 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7780.83 | 19.571 | [14 empty] | 106.6436 |  | 0.019001
| 40098.1114 | 59.977 | 3738.8787 |  |  | 3090 | 23.6888 | 22.5092 |  | 0 | 3788.4907 | 3767.9554 | 3783.957 | 3770.5065 | 3749.8109 |  |  |  |  | 40098.1114 | 59.977 | 3738.8787 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7781.16 | 23.6888 | [14 empty] | 106.8162 |  | 0.022999
| 40098.1114 | 59.974 | 3739.8596 |  |  | 3090 | 26.781 | 24.0044 |  | 0 | 3789.9858 | 3767.8837 | 3783.9723 | 3770.5065 | 3749.8638 |  |  |  |  | 40098.1114 | 59.974 | 3739.8596 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7781.49 | 26.781 | [14 empty] | 107.7972 |  | 0.026001
| 40098.1114 | 59.971 | 3738.1016 |  |  | 3090 | 29.8693 | 26.0571 |  | 0 | 3792.0386 | 3767.8079 | 3783.9929 | 3770.5065 | 3749.9165 |  |  |  |  | 40098.1114 | 59.971 | 3738.1016 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7781.82 | 29.8693 | [14 empty] | 106.0391 |  | 0.028999
| 40098.1115 | 59.971 | 3738.5579 |  |  | 3090 | 29.8693 | 27.3914 |  | 0 | 3793.3729 | 3767.7337 | 3784.0167 | 3770.5065 | 3749.9689 |  |  |  |  | 40098.1115 | 59.971 | 3738.5579 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7782.15 | 29.8693 | [14 empty] | 106.4954 |  | 0.028999
| 40098.1115 | 59.971 | 3743.5068 |  |  | 3090 | 29.8693 | 28.2586 |  | 0 | 3794.2401 | 3767.6723 | 3784.0426 | 3770.5065 | 3750.021 |  |  |  |  | 40098.1115 | 59.971 | 3743.5068 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7782.48 | 29.8693 | [14 empty] | 111.4444 |  | 0.028999
| 40098.1115 | 59.972 | 3743.4187 |  |  | 3090 | 28.8399 | 28.4621 |  | 0 | 3794.4436 | 3767.6111 | 3784.0688 | 3770.5065 | 3750.0729 |  |  |  |  | 40098.1115 | 59.972 | 3743.4187 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7782.81 | 28.8399 | [14 empty] | 111.3563 |  | 0.028
| 40098.1115 | 59.968 | 3745.2507 |  |  | 3090 | 32.9615 | 30.0369 |  | 0 | 3796.0184 | 3767.5548 | 3784.0989 | 3770.5065 | 3750.1245 |  |  |  |  | 40098.1115 | 59.968 | 3745.2507 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7783.14 | 32.9615 | [14 empty] | 113.1883 |  | 0.032001
| 40098.1116 | 59.966 | 3745.7441 |  |  | 3090 | 35.0204 | 31.7811 |  | 0 | 3797.7626 | 3767.5 | 3784.1333 | 3770.5065 | 3750.1758 |  |  |  |  | 40098.1116 | 59.966 | 3745.7441 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7783.47 | 35.0204 | [14 empty] | 113.6817 |  | 0.034
| 40098.1116 | 59.966 | 3747.3396 |  |  | 3090 | 35.0204 | 32.9149 |  | 0 | 3798.8964 | 3767.4494 | 3784.1703 | 3770.5065 | 3750.2269 |  |  |  |  | 40098.1116 | 59.966 | 3747.3396 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7783.8 | 35.0204 | [14 empty] | 115.2772 |  | 0.034
| 40098.1116 | 59.971 | 3750.7002 |  |  | 3090 | 29.8693 | 31.8489 |  | 0 | 3797.8304 | 3767.4076 | 3784.2044 | 3770.5065 | 3750.2777 |  |  |  |  | 40098.1116 | 59.971 | 3750.7002 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7784.13 | 29.8693 | [14 empty] | 118.6378 |  | 0.028999
| 40098.1116 | 59.973 | 3749.75 |  |  | 3090 | 27.8104 | 30.4355 |  | 0 | 3796.4169 | 3767.3635 | 3784.2349 | 3770.5065 | 3750.3283 |  |  |  |  | 40098.1116 | 59.973 | 3749.75 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7784.46 | 27.8104 | [14 empty] | 117.6876 |  | 0.027
| 40098.1116 | 59.972 | 3746.2166 |  |  | 3090 | 28.8399 | 29.877 |  | 0 | 3795.8585 | 3767.3109 | 3784.2638 | 3770.5065 | 3750.3786 |  |  |  |  | 40098.1116 | 59.972 | 3746.2166 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7784.79 | 28.8399 | [14 empty] | 114.1541 |  | 0.028
| 40098.1117 | 59.969 | 3744.6826 |  |  | 3090 | 31.9282 | 30.5949 |  | 0 | 3796.5764 | 3767.2548 | 3784.2943 | 3770.5065 | 3750.4287 |  |  |  |  | 40098.1117 | 59.969 | 3744.6826 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7785.12 | 31.9282 | [14 empty] | 112.6202 |  | 0.030998
| 40098.1117 | 59.972 | 3743.7451 |  |  | 3090 | 28.8399 | 29.9806 |  | 0 | 3795.9621 | 3767.1966 | 3784.3232 | 3770.5065 | 3750.4785 |  |  |  |  | 40098.1117 | 59.972 | 3743.7451 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7785.45 | 28.8399 | [14 empty] | 111.6827 |  | 0.028
| 40098.1117 | 59.974 | 3743.1489 |  |  | 3090 | 26.781 | 28.8608 |  | 0 | 3794.8423 | 3767.1372 | 3784.3492 | 3770.5065 | 3750.5281 |  |  |  |  | 40098.1117 | 59.974 | 3743.1489 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7785.78 | 26.781 | [14 empty] | 111.0865 |  | 0.026001
| 40098.1117 | 59.973 | 3740.2986 |  |  | 3090 | 27.8104 | 28.4932 |  | 0 | 3794.4746 | 3767.0711 | 3784.3741 | 3770.5065 | 3750.5774 |  |  |  |  | 40098.1117 | 59.973 | 3740.2986 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7786.11 | 27.8104 | [14 empty] | 108.2361 |  | 0.027
| 40098.1118 | 59.97 | 3739.4526 |  |  | 3090 | 30.8987 | 29.3351 |  | 0 | 3795.3166 | 3767.0032 | 3784.401 | 3770.5065 | 3750.6265 |  |  |  |  | 40098.1118 | 59.97 | 3739.4526 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7786.44 | 30.8987 | [14 empty] | 107.3902 |  | 0.029999
| 40098.1118 | 59.971 | 3733.376 |  |  | 3090 | 29.8693 | 29.5221 |  | 0 | 3795.5036 | 3766.9208 | 3784.4282 | 3770.5065 | 3750.6753 |  |  |  |  | 40098.1118 | 59.971 | 3733.376 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7786.77 | 29.8693 | [14 empty] | 101.3135 |  | 0.028999
| 40098.1118 | 59.974 | 3731.8296 |  |  | 3090 | 26.781 | 28.5627 |  | 0 | 3794.5442 | 3766.835 | 3784.453 | 3770.5065 | 3750.7239 |  |  |  |  | 40098.1118 | 59.974 | 3731.8296 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7787.1 | 26.781 | [14 empty] | 99.7672 |  | 0.026001
| 40098.1118 | 59.982 | 3737.5825 |  |  | 3090 | 18.5416 | 25.0553 |  | 0 | 3791.0368 | 3766.7637 | 3784.469 | 3770.5065 | 3750.7723 |  |  |  |  | 40098.1118 | 59.982 | 3737.5825 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7787.43 | 18.5416 | [14 empty] | 105.5201 |  | 0.018002
| 40098.1119 | 59.985 | 3736.2295 |  |  | 3090 | 15.4494 | 21.6932 |  | 0 | 3787.6747 | 3766.6894 | 3784.4768 | 3770.5065 | 3750.8204 |  |  |  |  | 40098.1119 | 59.985 | 3736.2295 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7787.76 | 15.4494 | [14 empty] | 104.1671 |  | 0.014999
| 40098.1119 | 59.985 | 3734.8967 |  |  | 3090 | 15.4494 | 19.5079 |  | 0 | 3785.4894 | 3766.6122 | 3784.4793 | 3770.5065 | 3750.8683 |  |  |  |  | 40098.1119 | 59.985 | 3734.8967 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7788.09 | 15.4494 | [14 empty] | 102.8343 |  | 0.014999
| 40098.1119 | 59.985 | 3733.4338 |  |  | 3090 | 15.4494 | 18.0874 |  | 0 | 3784.0689 | 3766.5319 | 3784.4783 | 3770.5065 | 3750.916 |  |  |  |  | 40098.1119 | 59.985 | 3733.4338 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7788.42 | 15.4494 | [14 empty] | 101.3714 |  | 0.014999
| 40098.1119 | 59.987 | 3733.1152 |  |  | 3090 | 13.3905 | 16.4435 |  | 0 | 3782.425 | 3766.4512 | 3784.4733 | 3770.5065 | 3750.9634 |  |  |  |  | 40098.1119 | 59.987 | 3733.1152 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7788.75 | 13.3905 | [14 empty] | 101.0528 |  | 0.013
| 40098.1119 | 59.989 | 3730.5098 |  |  | 3090 | 11.3316 | 14.6543 |  | 0 | 3780.6358 | 3766.3646 | 3784.4641 | 3770.5065 | 3751.0106 |  |  |  |  | 40098.1119 | 59.989 | 3730.5098 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7789.08 | 11.3316 | [14 empty] | 98.4473 |  | 0.011002
| 40098.112 | 59.989 | 3729.1802 |  |  | 3090 | 11.3316 | 13.4914 |  | 0 | 3779.4729 | 3766.2752 | 3784.4521 | 3770.5065 | 3751.0576 |  |  |  |  | 40098.112 | 59.989 | 3729.1802 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7789.41 | 11.3316 | [14 empty] | 97.1177 |  | 0.011002
| 40098.112 | 59.986 | 3725.4587 |  |  | 3090 | 14.4199 | 13.8164 |  | 0 | 3779.7979 | 3766.1773 | 3784.4409 | 3770.5065 | 3751.1044 |  |  |  |  | 40098.112 | 59.986 | 3725.4587 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7789.74 | 14.4199 | [14 empty] | 93.3963 |  | 0.014
| 40098.112 | 59.987 | 3724.7847 |  |  | 3090 | 13.3905 | 13.6673 |  | 0 | 3779.6488 | 3766.0783 | 3784.4294 | 3770.5065 | 3751.1509 |  |  |  |  | 40098.112 | 59.987 | 3724.7847 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7790.07 | 13.3905 | [14 empty] | 92.7222 |  | 0.013
| 40098.112 | 59.99 | 3720.1079 |  |  | 3090 | 10.2983 | 12.4882 |  | 0 | 3778.4696 | 3765.9685 | 3784.4152 | 3770.5065 | 3751.1972 |  |  |  |  | 40098.112 | 59.99 | 3720.1079 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7790.4 | 10.2983 | [14 empty] | 88.0455 |  | 0.0099983
| 40098.1121 | 59.994 | 3720.9382 |  |  | 3090 | 6.1805 | 10.2805 |  | 0 | 3776.262 | 3765.8613 | 3784.3958 | 3770.5065 | 3751.2433 |  |  |  |  | 40098.1121 | 59.994 | 3720.9382 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7790.73 | 6.1805 | [14 empty] | 88.8758 |  | 0.0060005
| 40098.1121 | 59.996 | 3725.6614 |  |  | 3090 | 4.1217 | 8.1249 |  | 0 | 3774.1064 | 3765.7658 | 3784.3714 | 3770.5065 | 3751.2891 |  |  |  |  | 40098.1121 | 59.996 | 3725.6614 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7791.06 | 4.1217 | [14 empty] | 93.5989 |  | 0.0040016
| 40098.1121 | 60.001 | 3725.6768 |  |  | 3090 | -1.0294 | 4.9209 |  | 0 | 3770.9024 | 3765.6708 | 3784.3395 | 3770.5065 | 3751.3348 |  |  |  |  | 40098.1121 | 60.001 | 3725.6768 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7791.39 | -1.0294 | [14 empty] | 93.6143 |  | 0.00099945
| 40098.1121 | 60.003 | 3727.7542 |  |  | 3090 | -3.0883 | 2.1177 |  | 0 | 3768.0992 | 3765.5812 | 3784.3011 | 3770.5065 | 3751.3802 |  |  |  |  | 40098.1121 | 60.003 | 3727.7542 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7791.72 | -3.0883 | [14 empty] | 95.6917 |  | 0.0029984
| 40098.1122 | 60.004 | 3727.8247 |  |  | 3090 | -4.1217 | -0.066099 |  | 0 | 3765.9154 | 3765.4922 | 3784.2577 | 3770.5065 | 3751.4254 |  |  |  |  | 40098.1122 | 60.004 | 3727.8247 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7792.05 | -4.1217 | [14 empty] | 95.7623 |  | 0.0040016
| 40098.1122 | 60.006 | 3727.6833 |  |  | 3090 | -6.1805 | -2.2062 |  | 0 | 3763.7753 | 3765.4032 | 3784.2095 | 3770.5065 | 3751.4704 |  |  |  |  | 40098.1122 | 60.006 | 3727.6833 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7792.38 | -6.1805 | [14 empty] | 95.6209 |  | 0.0060005
| 40098.1122 | 60.012 | 3727.2314 |  |  | 3090 | -12.3611 | -5.7604 |  | 0 | 3760.2211 | 3765.3136 | 3784.1532 | 3770.5065 | 3751.5152 |  |  |  |  | 40098.1122 | 60.012 | 3727.2314 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7792.71 | -12.3611 | [14 empty] | 95.169 |  | 0.012001
| 40098.1122 | 60.014 | 3725.0122 |  |  | 3090 | -14.4199 | -8.7912 |  | 0 | 3757.1903 | 3765.2192 | 3784.09 | 3770.5065 | 3751.5598 |  |  |  |  | 40098.1122 | 60.014 | 3725.0122 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7793.04 | -14.4199 | [14 empty] | 92.9498 |  | 0.014
| 40098.1122 | 60.019 | 3726.4463 |  |  | 3090 | -19.571 | -12.5642 |  | 0 | 3753.4173 | 3765.1286 | 3784.0184 | 3770.5065 | 3751.6042 |  |  |  |  | 40098.1122 | 60.019 | 3726.4463 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7793.37 | -19.571 | [14 empty] | 94.3839 |  | 0.019001
| 40098.1123 | 60.021 | 3726.0156 |  |  | 3090 | -21.6299 | -15.7372 |  | 0 | 3750.2443 | 3765.0374 | 3783.9397 | 3770.5065 | 3751.6483 |  |  |  |  | 40098.1123 | 60.021 | 3726.0156 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7793.7 | -21.6299 | [14 empty] | 93.9532 |  | 0.021
| 40098.1123 | 60.025 | 3719.123 |  |  | 3090 | -25.7516 | -19.2422 |  | 0 | 3746.7393 | 3764.9307 | 3783.8531 | 3770.5065 | 3751.6923 |  |  |  |  | 40098.1123 | 60.025 | 3719.123 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7794.03 | -25.7516 | [14 empty] | 87.0606 |  | 0.025002
| 40098.1123 | 60.026 | 3716.3745 |  |  | 3090 | -26.781 | -21.8808 |  | 0 | 3744.1007 | 3764.818 | 3783.7609 | 3770.5065 | 3751.7361 |  |  |  |  | 40098.1123 | 60.026 | 3716.3745 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7794.36 | -26.781 | [14 empty] | 84.3121 |  | 0.026001
| 40098.1123 | 60.027 | 3717.3325 |  |  | 3090 | -27.8104 | -23.9562 |  | 0 | 3742.0253 | 3764.7081 | 3783.6643 | 3770.5065 | 3751.7796 |  |  |  |  | 40098.1123 | 60.027 | 3717.3325 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7794.69 | -27.8104 | [14 empty] | 85.2701 |  | 0.027
| 40098.1124 | 60.029 | 3717.5598 |  |  | 3090 | -29.8693 | -26.0258 |  | 0 | 3739.9557 | 3764.5992 | 3783.5634 | 3770.5065 | 3751.823 |  |  |  |  | 40098.1124 | 60.029 | 3717.5598 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7795.02 | -29.8693 | [14 empty] | 85.4974 |  | 0.028999
| 40098.1124 | 60.029 | 3717.1421 |  |  | 3090 | -29.8693 | -27.371 |  | 0 | 3738.6105 | 3764.4899 | 3783.4598 | 3770.5065 | 3751.8661 |  |  |  |  | 40098.1124 | 60.029 | 3717.1421 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7795.35 | -29.8693 | [14 empty] | 85.0797 |  | 0.028999
| 40098.1124 | 60.037 | 3715.166 |  |  | 3090 | -38.1087 | -31.1292 |  | 0 | 3734.8523 | 3764.3765 | 3783.348 | 3770.5065 | 3751.9091 |  |  |  |  | 40098.1124 | 60.037 | 3715.166 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7795.68 | -38.1087 | [14 empty] | 83.1036 |  | 0.036999 | -103
| 40098.1124 | 60.036 | 3713.6318 |  |  | 3090 | -37.0793 | -33.2117 |  | 0 | 3732.7698 | 3764.2601 | 3783.232 | 3770.5065 | 3751.9518 |  |  |  |  | 40098.1124 | 60.036 | 3713.6318 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7796.01 | -37.0793 | [14 empty] | 81.5694 |  | 0.035999
| 40098.1125 | 60.037 | 3710.2834 |  |  | 3090 | -38.1087 | -34.9257 |  | 0 | 3731.0558 | 3764.1366 | 3783.1126 | 3770.5065 | 3751.9944 |  |  |  |  | 40098.1125 | 60.037 | 3710.2834 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7796.34 | -38.1087 | [14 empty] | 78.221 |  | 0.036999 | -103
| 40098.1125 | 60.037 | 3710.1577 |  |  | 3090 | -38.1087 | -36.0397 |  | 0 | 3729.9418 | 3764.0133 | 3782.9912 | 3770.5065 | 3752.0367 |  |  |  |  | 40098.1125 | 60.037 | 3710.1577 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7796.67 | -38.1087 | [14 empty] | 78.0953 |  | 0.036999 | -103
| 40098.1125 | 60.036 | 3699.3557 |  |  | 3090 | -37.0793 | -36.4036 |  | 0 | 3729.5779 | 3763.866 | 3782.8696 | 3770.5065 | 3752.0789 |  |  |  |  | 40098.1125 | 60.036 | 3699.3557 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7797 | -37.0793 | [14 empty] | 67.2933 |  | 0.035999
| 40098.1125 | 60.041 | 3698.5911 |  |  | 3090 | -42.2304 | -38.443 |  | 0 | 3727.5385 | 3763.7177 | 3782.7438 | 3770.5065 | 3752.1209 |  |  |  |  | 40098.1125 | 60.041 | 3698.5911 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7797.33 | -42.2304 | [14 empty] | 66.5286 |  | 0.041 | -103
| 40098.1125 | 60.043 | 3704.5913 |  |  | 3090 | -44.2892 | -40.4892 |  | 0 | 3725.4923 | 3763.5836 | 3782.614 | 3770.5065 | 3752.1627 |  |  |  |  | 40098.1125 | 60.043 | 3704.5913 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7797.66 | -44.2892 | [14 empty] | 72.5289 |  | 0.042999 | -103
| 40098.1126 | 60.044 | 3703.2754 |  |  | 3090 | -45.3187 | -42.1795 |  | 0 | 3723.802 | 3763.4472 | 3782.4809 | 3770.5065 | 3752.2043 |  |  |  |  | 40098.1126 | 60.044 | 3703.2754 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7797.99 | -45.3187 | [14 empty] | 71.213 |  | 0.043999 | -103
| 40098.1126 | 60.043 | 3702.4824 |  |  | 3090 | -44.2892 | -42.9179 |  | 0 | 3723.0636 | 3763.3096 | 3782.3468 | 3770.5065 | 3752.2457 |  |  |  |  | 40098.1126 | 60.043 | 3702.4824 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7798.32 | -44.2892 | [14 empty] | 70.42 |  | 0.042999 | -103
| 40098.1126 | 60.046 | 3701.3164 |  |  | 3090 | -47.3815 | -44.4802 |  | 0 | 3721.5013 | 3763.1699 | 3782.2098 | 3770.5065 | 3752.2869 |  |  |  |  | 40098.1126 | 60.046 | 3701.3164 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7798.65 | -47.3815 | [14 empty] | 69.254 |  | 0.046001 | -103
| 40098.1126 | 60.048 | 3700.8259 |  |  | 3090 | -49.4403 | -46.2162 |  | 0 | 3719.7653 | 3763.0298 | 3782.0694 | 3770.5065 | 3752.3279 |  |  |  |  | 40098.1126 | 60.048 | 3700.8259 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7798.98 | -49.4403 | [14 empty] | 68.7635 |  | 0.048 | -103
| 40098.1127 | 60.046 | 3699.5286 |  |  | 3090 | -47.3815 | -46.6241 |  | 0 | 3719.3574 | 3762.8875 | 3781.9288 | 3770.5065 | 3752.3688 |  |  |  |  | 40098.1127 | 60.046 | 3699.5286 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7799.31 | -47.3815 | [14 empty] | 67.4661 |  | 0.046001 | -103
| 40098.1127 | 60.046 | 3699.7261 |  |  | 3090 | -47.3815 | -46.8892 |  | 0 | 3719.0923 | 3762.7462 | 3781.7883 | 3770.5065 | 3752.4094 |  |  |  |  | 40098.1127 | 60.046 | 3699.7261 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7799.64 | -47.3815 | [14 empty] | 67.6636 |  | 0.046001 | -103
| 40098.1127 | 60.043 | 3690.0996 |  |  | 3090 | -44.2892 | -45.9792 |  | 0 | 3720.0023 | 3762.584 | 3781.6503 | 3770.5065 | 3752.4499 |  |  |  |  | 40098.1127 | 60.043 | 3690.0996 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7799.97 | -44.2892 | [14 empty] | 58.0372 |  | 0.042999 | -103
| 40098.1127 | 60.043 | 3690.4773 |  |  | 3090 | -44.2892 | -45.3877 |  | 0 | 3720.5938 | 3762.4234 | 3781.5144 | 3770.5065 | 3752.4902 |  |  |  |  | 40098.1127 | 60.043 | 3690.4773 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7800.3 | -44.2892 | [14 empty] | 58.4149 |  | 0.042999 | -103
| 40098.1128 | 60.044 | 3696.8645 |  |  | 3090 | -45.3187 | -45.3635 |  | 0 | 3720.6179 | 3762.2777 | 3781.379 | 3770.5065 | 3752.5304 |  |  |  |  | 40098.1128 | 60.044 | 3696.8645 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7800.63 | -45.3187 | [14 empty] | 64.8021 |  | 0.043999 | -103
| 40098.1128 | 60.043 | 3696.8772 |  |  | 3090 | -44.2892 | -44.9875 |  | 0 | 3720.9939 | 3762.1327 | 3781.2451 | 3770.5065 | 3752.5703 |  |  |  |  | 40098.1128 | 60.043 | 3696.8772 | 350 | -223.0157 | 16 |  | 10 | 0 | -103 | 7800.96 | -44.2892 | [14 empty] | 64.8148 |  | 0.042999 | -103
Note on L13: TC allowable range 0.050 to 1.000 with 1.0 turning filter off. Beginning Target slope should align with Actual slope.

## Graph 20 to 52s
# of rows to shift T(0)
2
A zero value aligns the data to the hightest Frequency change value.
Usually the event begins one or two data scans earlier than this scan.
Increasing this value shifts graph data to the right.
Decreasing this value shifts graph data to the left.
Note: The P.U. Performance values indicate performance as a P.U. value of BA Bias setting.
For BAs that utilize a variable Bias, the Bias average during T(+20) to T(+52) is used.
P.U. values above 1.0 indicate that the Bias setting was below measured Frequency Response.
P.U. values below 1.0 indicate that the Bias setting was above measured Frequency Response.
T(0)
First change in frequency of the event should occur here on the vertical grid line.
It is important that the pre-event frequency average to NOT contain frequency data of the event, "Average Frequency" trend to the left of center of the graph.
To shift the data on the graph left or right, adjust the value in cell Q3 highlighted in yellow above.

## Sustained Graph
The Target Trend provides an indication of "Expected Primary
Frequency Response" based on the BA's Bias setting.
The Target assumes a straight line ramp from the beginning
of the event until event frequency recovery. The Target then
adds the Primay Frequency Response expectation of the
BA's Bias based on frequency during the recovery period.
If the Bias setting is slightly higher than actual Primary Frequency
Response, the Target Trend should be above the "Interchange
MW" Trend if the event was a low frequency event.

## Bias Graph
This graph provides a comparison of the BA's Bias Setting
to the actual Primary Frequency Response. Evaluation beyond
the first minute or two could include Secondary control and
the BA should not consider the data a true representation
of Primary Frequency Response without further evaluation.

## Form 1 Summary Data
[6 empty] | Value A Data |  | BA Performance | [8 empty] | Value B | 20 to 52 second Average Period Evaluation | [13 empty] | Frequency Response Initiative - Additional Primary Frequency Response Evaluation Points
[8 empty] | JOU | Non- |  |  | Transferred | Contingent | [5 empty] | JOU | Non- |  |  | Transferred | Contingent | [6 empty] | Average | Unadjusted | Unadjusted | Unadjusted | Unadjusted | Unadjusted | Adjusted | Adjusted | Adjusted | Adjusted | Adjusted
Date | A Value | FPointA | A Value | t(0) Time | C Value |  | Net | Dynamic | Conforming | Pumped | Not | Frequency | BA | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Not | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias | Bias While | PFR | PFR | PFR | PFR | PFR | PFR | PFR | PFR | PFR | PFR
| Time | Hz | Hz |  | Hz |  | Actual | Schedules | Load | Hydro | Used | Response | Lost Generation | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Used | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting | Hz > +/-0.036 | Performance | Performance | Performance | Performance | Performance | Performance | Performance | Performance | Performance | Performance | Maximum | Minimum
[6 empty] | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) |  | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) |  | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Hz | @ T(+46) | @ T(+76) | @ T(+106) | @ T(+136) | @ T(+166) | @ T(+46) | @ T(+76) | @ T(+106) | @ T(+136) | @ T(+166) | Bias Setting | Bias Setting
[6 empty] | Hz | MW | MW | MW | MW |  | MW | MW | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW |  | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | MW/0.1 Hz | P.U. | P.U. | P.U. | P.U. | P.U. | P.U. | P.U. | P.U. | P.U. | P.U. | MW/0.1 Hz | MW/0.1 Hz
2009-10-12 02:27 | 40098.1024 | 60.041 | 60.0421 | 40098.1024 | 59.836 | 60.0421 | 3647.0624 | 350 | -165.4764 | 0 | 0 | -4.2125 | 15 | -103 | 7650.975 | -43.389 | 59.8891 | 3788.3545 | 335 | -216.2155 | 12.7647 | 0 | 11.0882 | 0 | 1.0425 | 0.99172 | 0.84493 | -103 | 7632 | 114.2087 | -103 | 1.5194 | 1.3893 | 1.7127 | 1.7369 | 2.0593 | 1.5696 | 1.4646 | 1.8858 | 1.8739 | 2.4021 | -103 | -1538

## Instructions
Steps | To be completed for each event evaluated.
1 | Set-up Data collection in exact same order as the "Data" sheet of this work book. Data should be in this order: (See special instructions for column A data on the "Copy Data" worksheet)
Column A: Date and Time in this format, mm/dd/yy HH:MM:SS
Column B: Frequency Hz
Column C: Net Actual Interchange
Column D: Joint Owned Unit dynamic schedule
Column E: Non Conforming Load
Column F: Pumped Hydro
Column G: Not Used
Column H: Transferred Frequency Response
Column I: Contingent BA Lost load or generation
Column J: BA Bias Setting
Column K: BA Load
2 | Note: Columns D, E, F and H are optional data. If you choose not to use these, leave the columns blank. Do not delete the columns. Use the sign (+/-) convention defined in FRS Form 1.
3 | Data compression must be turned off for each data point. Quality data will give you quality results in the evaluation.
4 | Data must start a minimum of two (2) minutes before the event begins and includes a minimum of 15 minutes after the beginning of the event with up to 60 minutes of data.
Be sure the "Data" worksheet is clear of any old data and extra formulas in columns M through R below your data. Collect the same total minutes of data for each event evaluated to minimize your effort and time.
If using PI historian as your data source, use "PasteSpecial/Values" to enter data into the spreadsheet. Do not include historian data collection formulas in the data.
5 | Verify that the "Auto" Event Detection selected the correct event. Verify time and delta Hz by comparing time of event and delta Hz on the graph on the "Copy Results" worksheet.
If the wrong event was selected, in cell "E4" of this worksheet select "Manual" and manually select the beginning and ending row numbers of the desired event and enter these in cells "E5" and "E6". Only rarely should you have to use the "Manual" process.
6 | Once data is in place in the "Data" worksheet, confirm the Auto selection of the beginning of the event by observing the "Graph 20 to 52s" worksheet. Adjust the selection if necessary.
To make an adjustment, change the value in cell "Q3" on the "Graph 20 to 52s" worksheet. Usually a 0, 1 or 2 will achieve the correct alignment of T(0).
7 | If the correct row is selected, the "Graph 20 to 52s" worksheet will indicate the first change in frequency (red trend) of the event on the center vertical grid line of the graph.
8 | The end of the event will be Auto selected based on the frequency value in cell "N2" on the Data worksheet. This will be the frequency at the beginning of the event or 60 Hz, whichever is lower. (for low Hz events)
This value controls the end of the "Sustained Frequency Response" evaluation period.
Primary Frequency Response should be sustained during the event recovery period. This evaluation determines how well you achieved this goal.
9 | Use the "Copy Form 2 data for Pasting into Form 1" button provided on the "Copy Results" worksheet (Cells B21 through B28) to copy the evaluation and event specific data for the "FRS Form 1" of this field trial. This data is summarized
in the correct order on worksheet "Form 1 Summary Data".
10 | Use PasteSpecial/Values and paste the copied data into FRS Form 1 on the appropriate event row. Be sure to use the latest version of Form 1, currently Form 1.9.
11 | Save this Form 2 using the file name convention on the "Copy Results" worksheet. The complete file name is in bold in cell B38. Return all completed Form 2s with your Form 1 to NERC.
Steps | To be completed the first time you use Form 2 for your BA.
A | Enter the Balancing Authority name as you want it to appear on the graphs in cell "B1" of the "Copy Results" worksheet. For example: "NYISO".
B | For informational and educational purposes, a "Sustained" performance evaluation is provided in the "Evaluation" worksheet and visually in the "Sustained Graph" worksheet. This evaluation uses a Time Constant (TC) to model the frequency response of your BA.
The time constant is located in cell "L13" of the "Evaluation" spreadsheet and should be edited for the types of generators in your BA. Presently this time constant is set at 0.35.
The higher the value of the time constant, the faster the delivery of frequency response is expected. Setting the TC to 1.0 effectively turns off the delay and instantaneous frequency response will be modeled. Do not set higher than 1.0.
This time constant is only used in the "Sustained" evaluation and is not used for the Field Trial evaluation of performance to the FRO.
A typical setting for this time constant is 0.08 to 0.15 for hydro units, 0.10 to 0.20 for large steam turbines and 0.20 to 0.40 for combustion turbines.
By observing the slope of your "Interchange Actual" on the "Sustained" Graph, adjust the time constant until the initial slope of the "Target" is similar to the slope of the NAI data.
When set appropriately, the "Target" trend on the "Sustained" graph will model what the Net Actual Interchange should have done during the event recovery period based on your Bias setting during the event.

## Adj Graph JOU
During Low Frequency events, MW data going from more positive to
less positive values will decrease the PFR measure on Form 1.
Balancing Authorities that use Dynamic Scheduling or Pseudo-ties for jointly owned units shall reflect their respective share of the unit governor droop response in their respective Frequency Bias Setting.
Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C).
The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting.

## Adj Graph NCL
For Low Frequency events, Load that "increases", goes more negative,
will adjust to improve measured Primary Frequency
Response on Form 1.
For Low Frequency events, Load that "decreases", goes less negative,
Will adjust to decrease measured Primary Frequency
Response on Form 1.
If your Non-conforming load data is positive, cell "Z1" on the Evaluation
worksheet can be changed to a "+" to invert the adjustment.

## Revision Change History
Date | Industry Body Approving Change | File Name | Changes
2012-11-20 | Standard Drafting Team | FRS Form 2.9a | 1. Included Contingent BA MW loss adjustment in both the "Un-adjusted" and "Adjusted" P.U. measures.
2. Added additional P.U. evaluation as recommended in the Frequency Response Initiative Report. (For information purposes only.)
3. Added "Auto" event detection with the ability to make fine adjustments for proper data alignment.
2012-12-02 | Standard Drafting Team | FRS Form 2.9a With Special DATE and TIME Data Fill | 1. Added Date Time Auto fill for non-Excel format Date Time data.